## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 17 | 16 | 23 | 20 | 5.9 | 19.61 | 50 | 72.7 | 14.8 | 26.9 | 37.6 | 224.3 | 220.3 | 220.3 | YES
2 | OK | 16 | 19 | 23 | 20 | 5.9 | 19.1 | 50 | 72.7 | 14.8 | 28.1 | 37 | 224.3 | 220.4 | 220.4 | YES
3 | OK | 19 | 18 | 23 | 20 | 5.9 | 19.1 | 50 | 72.7 | 14.8 | 28.1 | 37 | 224.3 | 220.4 | 220.4 | YES
4 | OK | 18 | 20 | 23 | 20 | 5.9 | 19.01 | 50 | 72.7 | 14.8 | 28.3 | 36.9 | 224.3 | 220.4 | 220.4 | YES
5 | OK | 20 | 21 | 23 | 20 | 5.9 | 19.01 | 50 | 72.7 | 14.8 | 28.3 | 36.3 | 224.3 | 220.5 | 220.5 | YES
6 | OK | 21 | 27 | 28 | 20 | 79 | 1.71 | 50 | 72.7 | 14.8 | 68.7 | 16.8 | 218 | 222.2 | 218 | YES
7 | OK | 21 | 29 | 23 | 20 | 5.9 | 16.83 | 50 | 72.7 | 14.8 | 33.3 | 34.3 | 224.3 | 220.9 | 220.9 | YES
8 | OK | 29 | 24 | 23 | 20 | 5.9 | 14.07 | 50 | 72.7 | 14.8 | 39.7 | 31.1 | 223 | 220.9 | 220.9 | YES
9 | OK | 24 | 25 | 26 | 20 | 24 | 2.3 | 50 | 72.7 | 14.8 | 67.3 | 17.5 | 215.9 | 222.6 | 215.9 | YES
10 | ** OPTIMAL ** | 24 | 22 | 23 | 20 | 5.9 | 1.72 | 50 | 72.7 | 14.8 | 51.2 | 16.8 | 221.8 | 222.6 | 221.8 | YES
11 | OK | 25 | 26 | 26 | 20 | 24 | 1.6 | 50 | 72.7 | 14.8 | 69 | 14.8 | 215.9 | 222.6 | 215.9 | YES
12 | OK | 22 | 23 | 23 | 20 | 5.9 | 0.28 | 50 | 72.7 | 14.8 | 72.1 | 15.2 | 216 | 222.6 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-005400
TR_B (available) | 68-015313
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 72.7
TR_B Baseline Loading% | 14.8
Total Scenarios Evaluated | 12
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 22
Tie Node (TR_A side) | 23
Tie Node (TR_B side) | 20
Tie Line Distance (m) | 5.9
Load Transferred (kW) | 1.72
TR_A Loading After (%) | 51.2
TR_B Loading After (%) | 16.8
Minimum Voltage (V) | 221.8