## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 7 | 5 | 81 | 16 | 1.8 | 11.93 | 50 | 97.7 | 14.7 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
| NG | 7 | 9 | 37 | 23 | 127.9 | 9.6 | 50 | 97.7 | 14.7 | 60.9 | 76.4 | 216.4 | 186.8 | 186.8 | NO
| NG | 5 | 6 | 81 | 16 | 1.8 | 11.32 | 50 | 97.7 | 14.7 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
| NG | 9 | 10 | 37 | 23 | 127.9 | 6.23 | 50 | 97.7 | 14.7 | [5 empty] | NO | TR_A sim: not converged
| NG | 6 | 4 | 81 | 16 | 1.8 | 11.32 | 50 | 97.7 | 14.7 | 46.4 | 83.5 | 224.2 | 195.8 | 195.8 | NO
| NG | 10 | 11 | 37 | 23 | 127.9 | 6.23 | 50 | 97.7 | 14.7 |  | 52.8 | 34763905175.1 | 203.1 | 203.1 | NO
| NG | 4 | 3 | 81 | 16 | 1.8 | 9.65 | 50 | 97.7 | 14.7 | 59.6 | 72.6 | 222 | 202 | 202 | NO
| NG | 11 | 15 | 37 | 23 | 127.9 | 5.56 | 50 | 97.7 | 14.7 | 0 | 48.4 | 5.0808e+58 | 206 | 206 | NO
| NG | 3 | 19 | 81 | 16 | 1.8 | 8.84 | 50 | 97.7 | 14.7 | 62.7 | 67.4 | 222 | 204.2 | 204.2 | NO
| NG | 19 | 2 | 81 | 16 | 1.8 | 7.68 | 50 | 97.7 | 14.7 | 62.7 | 60.2 | 222 | 207.3 | 207.3 | NO
1 | OK | 2 | 42 | 81 | 16 | 1.8 | 6.37 | 50 | 97.7 | 14.7 | 72.7 | 52.1 | 219.5 | 210.6 | 210.6 | YES
2 | OK | 42 | 43 | 81 | 16 | 1.8 | 5.73 | 50 | 97.7 | 14.7 | 75.2 | 48.3 | 219.5 | 212.1 | 212.1 | YES
3 | ** OPTIMAL ** | 43 | 44 | 81 | 16 | 1.8 | 5.69 | 50 | 97.7 | 14.7 | 75.3 | 48 | 219.5 | 212.2 | 212.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-005763
TR_B (available) | 29-014565
TR_A Rated kVA | 30
TR_B Rated kVA | 20
TR_A Baseline Loading% | 97.7
TR_B Baseline Loading% | 14.7
Total Scenarios Evaluated | 13
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 43
Switch Child Node | 44
Tie Node (TR_A side) | 81
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 1.8
Load Transferred (kW) | 5.69
TR_A Loading After (%) | 75.3
TR_B Loading After (%) | 48
Minimum Voltage (V) | 212.2