## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 7 | 9 | 41 | 2 | 85 | 9.6 | 50 | 97.7 | 9.8 | 60.9 | 15.5 | 216.4 | 210.4 | 210.4 | YES
| NG | 9 | 10 | 41 | 2 | 85 | 6.23 | 50 | 97.7 | 9.8 | [5 empty] | NO | TR_A sim: not converged
| NG | 10 | 11 | 41 | 2 | 85 | 6.23 | 50 | 97.7 | 9.8 |  | 13.2 | 34763905175.1 | 216.4 | 216.4 | NO
2 | ** OPTIMAL ** | 11 | 15 | 41 | 2 | 85 | 5.56 | 50 | 97.7 | 9.8 | 0 | 12.4 | 5.0808e+58 | 218 | 218 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-005763
TR_B (available) | 62-005042
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 97.7
TR_B Baseline Loading% | 9.8
Total Scenarios Evaluated | 4
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 15
Tie Node (TR_A side) | 41
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 85
Load Transferred (kW) | 5.56
TR_A Loading After (%) | 0
TR_B Loading After (%) | 12.4
Minimum Voltage (V) | 218