## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 25 | 26 | 1 | 6.1 | 11.04 | 50 | 90.3 | 12.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 55 | 33 | 33 | 1 | 46.5 | 27.82 | 50 | 90.3 | 12.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 25 | 26 | 26 | 1 | 6.1 | 10.58 | 50 | 90.3 | 12.9 | 65.8 | 20.9 | 214.1 | 216.5 | 214.1 | YES
| NG | 33 | 34 | 34 | 1 | 64.8 | 26.26 | 50 | 90.3 | 12.9 | 29.1 | 32.9 | 222 | 204 | 204 | NO
2 | OK | 26 | 44 | 44 | 1 | 38.6 | 8.19 | 50 | 90.3 | 12.9 | 71.3 | 19 | 214.1 | 219.2 | 214.1 | YES
3 | OK | 34 | 36 | 36 | 1 | 71.1 | 20.16 | 50 | 90.3 | 12.9 | 43.1 | 28.1 | 221.6 | 211.4 | 211.4 | YES
4 | OK | 44 | 43 | 43 | 0 | 73.6 | 5.66 | 50 | 90.3 | 12.9 | 77.1 | 17.1 | 214.1 | 220.7 | 214.1 | YES
5 | OK | 36 | 3 | 3 | 1 | 84.8 | 20.16 | 50 | 90.3 | 12.9 | 43.1 | 28.1 | 221.6 | 211.4 | 211.4 | YES
6 | OK | 3 | 4 | 65 | 23 | 120.6 | 19.62 | 50 | 90.3 | 12.9 | 44.4 | 15.4 | 221.6 | 225 | 221.6 | YES
7 | OK | 4 | 5 | 65 | 23 | 120.6 | 17.51 | 50 | 90.3 | 12.9 | 49.3 | 15.4 | 221.6 | 225 | 221.6 | YES
8 | ** OPTIMAL ** | 5 | 7 | 65 | 23 | 120.6 | 16.35 | 50 | 90.3 | 12.9 | 52 | 15.4 | 221.6 | 225 | 221.6 | YES
9 | OK | 7 | 6 | 65 | 23 | 120.6 | 15.31 | 50 | 90.3 | 12.9 | 54.4 | 15.1 | 221.4 | 225.4 | 221.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-007091
TR_B (available) | 45-015560
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 90.3
TR_B Baseline Loading% | 12.9
Total Scenarios Evaluated | 12
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 7
Tie Node (TR_A side) | 65
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 120.6
Load Transferred (kW) | 16.35
TR_A Loading After (%) | 52
TR_B Loading After (%) | 15.4
Minimum Voltage (V) | 221.6