## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 55 | 25 | 28 | 4 | 10.2 | 11.04 | 50 | 90.3 | 53.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 25 | 26 | 28 | 4 | 10.2 | 10.58 | 50 | 90.3 | 53.3 | 65.8 | 77.9 | 214.1 | 216.8 | 214.1 | YES
2 | OK | 26 | 44 | 44 | 24 | 71.3 | 8.19 | 50 | 90.3 | 53.3 | 71.3 | 72.4 | 214.1 | 217.8 | 214.1 | YES
3 | OK | 44 | 43 | 42 | 23 | 71.5 | 5.66 | 50 | 90.3 | 53.3 | 77.1 | 66.6 | 214.1 | 218.7 | 214.1 | YES
4 | OK | 6 | 14 | 15 | 30 | 32.7 | 10.95 | 50 | 90.3 | 53.3 | 64.4 | 59.7 | 221.3 | 218.3 | 218.3 | YES
5 | OK | 14 | 13 | 15 | 30 | 32.7 | 9.03 | 50 | 90.3 | 53.3 | 69 | 59.7 | 221.3 | 218.3 | 218.3 | YES
6 | OK | 13 | 15 | 15 | 30 | 32.7 | 8.22 | 50 | 90.3 | 53.3 | 70.9 | 59.1 | 221.1 | 218.8 | 218.8 | YES
7 | ** OPTIMAL ** | 15 | 30 | 30 | 30 | 32.7 | 7.53 | 50 | 90.3 | 53.3 | 72.5 | 59.1 | 221.1 | 218.8 | 218.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 62-007091
TR_B (available) | 45-021284
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 90.3
TR_B Baseline Loading% | 53.3
Total Scenarios Evaluated | 8
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 30
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 30
Tie Line Distance (m) | 32.7
Load Transferred (kW) | 7.53
TR_A Loading After (%) | 72.5
TR_B Loading After (%) | 59.1
Minimum Voltage (V) | 218.8