## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 62 | 61 | 64 | 70 | 1.8 | 33.41 | 50 | 76.7 | 40 | 37.9 | 50.3 | 209 | 185.6 | 185.6 | NO
| NG | 62 | 63 | 44 | 68 | 2.1 | 31.76 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 61 | 24 | 64 | 70 | 1.8 | 32.98 | 50 | 76.7 | 40 | 37.9 | 50.3 | 208.9 | 185.6 | 185.6 | NO
| NG | 63 | 60 | 44 | 68 | 2.1 | 31.76 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 24 | 25 | 25 | 67 | 39 | 10.76 | 50 | 76.7 | 40 | 63.7 | 43.4 | 207 | 220.2 | 207 | NO
| NG | 24 | 59 | 64 | 70 | 1.8 | 22.22 | 50 | 76.7 | 40 | 50.8 | 45.8 | 208.3 | 207 | 207 | NO
| NG | 60 | 58 | 44 | 68 | 2.1 | 31.76 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 25 | 65 | 31 | 85 | 67 | 10.76 | 50 | 76.7 | 40 | 64.2 | 49.5 | 207 | 182.3 | 182.3 | NO
| NG | 59 | 36 | 64 | 70 | 1.8 | 22.22 | 50 | 76.7 | 40 | 50.8 | 45.8 | 208.3 | 207 | 207 | NO
| NG | 58 | 57 | 51 | 67 | 6.2 | 0.55 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 40.0% (degenerate)
| NG | 58 | 5 | 44 | 68 | 2.1 | 31.21 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 65 | 46 | 31 | 85 | 67 | 10.76 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 40.0% (degenerate)
| NG | 36 | 35 | 64 | 70 | 1.8 | 20.59 | 50 | 76.7 | 40 | 52.7 | 45.8 | 208.3 | 207 | 207 | NO
| NG | 5 | 6 | 44 | 68 | 2.1 | 31.21 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 46 | 28 | 31 | 85 | 67 | 10.14 | 50 | 76.7 | 40 | 64.9 | 48.8 | 207 | 186 | 186 | NO
| NG | 35 | 26 | 64 | 70 | 1.8 | 18.41 | 50 | 76.7 | 40 | 55.1 | 45.7 | 208.5 | 207.7 | 207.7 | NO
| NG | 35 | 37 | 34 | 76 | 2.7 | 2.18 | 50 | 76.7 | 40 | 74.2 | 41.6 | 206.6 | 219.9 | 206.6 | NO
| NG | 6 | 7 | 44 | 68 | 2.1 | 29.77 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 28 | 29 | 31 | 85 | 67 | 6.85 | 50 | 76.7 | 40 | 68.8 | 45.5 | 207 | 202.9 | 202.9 | NO
| NG | 28 | 71 | 71 | 67 | 145.3 | 0.78 | 50 | 76.7 | 40 | 75.8 | 40.6 | 206.3 | 220.2 | 206.3 | NO
| NG | 26 | 27 | 64 | 70 | 1.8 | 15.1 | 50 | 76.7 | 40 | 59 | 44 | 208.1 | 214.5 | 208.1 | NO
| NG | 37 | 32 | 34 | 76 | 2.7 | 2.18 | 50 | 76.7 | 40 | 74.2 | 41.6 | 206.6 | 219.9 | 206.6 | NO
| NG | 7 | 8 | 44 | 68 | 2.1 | 27.18 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 29 | 30 | 31 | 85 | 67 | 4.77 | 50 | 76.7 | 40 | 71.2 | 43.7 | 207 | 211.6 | 207 | NO
| NG | 27 | 23 | 64 | 70 | 1.8 | 14.89 | 50 | 76.7 | 40 | 59.2 | 44 | 208 | 214.5 | 208 | NO
| NG | 32 | 33 | 34 | 76 | 2.7 | 1.15 | 50 | 76.7 | 40 | 75.4 | 40.9 | 206.6 | 220.2 | 206.6 | NO
| NG | 8 | 9 | 44 | 68 | 2.1 | 25.92 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 30 | 2 | 31 | 85 | 67 | 3.5 | 50 | 76.7 | 40 | 72.6 | 42.7 | 206.7 | 216.5 | 206.7 | NO
| NG | 23 | 22 | 64 | 70 | 1.8 | 13.68 | 50 | 76.7 | 40 | 60.6 | 44 | 207.7 | 214.5 | 207.7 | NO
| NG | 33 | 34 | 34 | 76 | 2.7 | 0.18 | 50 | 76.7 | 40 | 76.5 | 40.2 | 206.3 | 220.2 | 206.3 | NO
| NG | 9 | 40 | 44 | 68 | 2.1 | 25.92 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 2 | 3 | 1 | 85 | 92.3 | 1.28 | 50 | 76.7 | 40 | 75.2 | 41 | 206.7 | 220.2 | 206.7 | NO
| NG | 2 | 4 | 31 | 85 | 67 | 2.22 | 50 | 76.7 | 40 | 74.1 | 41.7 | 206.3 | 220.2 | 206.3 | NO
| NG | 22 | 21 | 64 | 70 | 1.8 | 13.05 | 50 | 76.7 | 40 | 61.3 | 44 | 207.7 | 214.5 | 207.7 | NO
| NG | 40 | 41 | 44 | 68 | 2.1 | 23.83 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 3 | 0 | 1 | 85 | 92.3 | 0.41 | 50 | 76.7 | 40 | 76.2 | 40.3 | 206.4 | 220.2 | 206.4 | NO
| NG | 4 | 31 | 31 | 85 | 67 | 2.22 | 50 | 76.7 | 40 | 74.1 | 41.7 | 206.3 | 220.2 | 206.3 | NO
| NG | 21 | 19 | 64 | 70 | 1.8 | 10.91 | 50 | 76.7 | 40 | 63 | 42.3 | 207.7 | 220.2 | 207.7 | NO
| NG | 41 | 53 | 44 | 68 | 2.1 | 22.55 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 0 | 1 | 1 | 85 | 92.3 | 0.41 | 50 | 76.7 | 40 | 76.2 | 40.3 | 206.4 | 220.2 | 206.4 | NO
| NG | 31 | 74 | 74 | 85 | 88.8 | 0.48 | 50 | 76.7 | 40 | 76.1 | 40.4 | 206.3 | 220.2 | 206.3 | NO
| NG | 19 | 20 | 64 | 70 | 1.8 | 10.52 | 50 | 76.7 | 40 | 64.3 | 42 | 207.7 | 220.2 | 207.7 | NO
| NG | 53 | 52 | 44 | 68 | 2.1 | 22.55 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: not converged
| NG | 74 | 86 | 86 | 85 | 109.9 | 0.36 | 50 | 76.7 | 40 | 76.3 | 40.3 | 206.3 | 220.2 | 206.3 | NO
| NG | 20 | 17 | 64 | 70 | 1.8 | 9.78 | 50 | 76.7 | 40 | 64.8 | 42 | 207.7 | 220.2 | 207.7 | NO
| NG | 52 | 45 | 44 | 68 | 2.1 | 19.04 | 50 | 76.7 | 40 | 124.3 | 61.4 | 6 | 139.3 | 6 | NO
| NG | 52 | 70 | 70 | 80 | 17.1 | 2.87 | 50 | 76.7 | 40 | 73.2 | 42.1 | 206.1 | 220.2 | 206.1 | NO
| NG | 17 | 18 | 64 | 70 | 1.8 | 9.78 | 50 | 76.7 | 40 | 65.1 | 42 | 207.7 | 220.2 | 207.7 | NO
| NG | 45 | 42 | 44 | 68 | 2.1 | 18.92 | 50 | 76.7 | 40 | 53.6 | 61 | 220.2 | 140.9 | 140.9 | NO
| NG | 70 | 66 | 69 | 53 | 51.9 | 2.42 | 50 | 76.7 | 40 | 73.8 | 41.8 | 206.1 | 220.2 | 206.1 | NO
| NG | 18 | 15 | 64 | 70 | 1.8 | 5.26 | 50 | 76.7 | 40 | 70.5 | 41.2 | 206.2 | 220.2 | 206.2 | NO
| NG | 18 | 93 | 93 | 70 | 108.6 | 4.52 | 50 | 76.7 | 40 | 71.3 | 43.5 | 207.8 | 214 | 207.8 | NO
| NG | 42 | 10 | 44 | 68 | 2.1 | 17.13 | 50 | 76.7 | 40 | 55.7 | 57.1 | 220.3 | 158.6 | 158.6 | NO
| NG | 66 | 67 | 69 | 53 | 51.9 | 1.97 | 50 | 76.7 | 40 | 74.3 | 41.5 | 206.1 | 220.2 | 206.1 | NO
| NG | 15 | 16 | 64 | 70 | 1.8 | 4.11 | 50 | 76.7 | 40 | 71.9 | 41.2 | 206.3 | 220.2 | 206.3 | NO
| NG | 93 | 56 | 56 | 70 | 132.1 | 4.44 | 50 | 76.7 | 40 | 71.4 | 43.4 | 207.7 | 215 | 207.7 | NO
| NG | 10 | 11 | 44 | 68 | 2.1 | 13.93 | 50 | 76.7 | 40 | 59.5 | 52.5 | 219 | 178.8 | 178.8 | NO
| NG | 67 | 68 | 69 | 53 | 51.9 | 0.86 | 50 | 76.7 | 40 | 75.7 | 40.7 | 206.2 | 220.2 | 206.2 | NO
| NG | 16 | 38 | 64 | 70 | 1.8 | 4.11 | 50 | 76.7 | 40 | 71.9 | 40.1 | 206.3 | 220.2 | 206.3 | NO
| NG | 56 | 54 | 94 | 70 | 142.9 | 4.41 | 50 | 76.7 | 40 | 71.5 | 43.4 | 207.7 | 215.2 | 207.7 | NO
| NG | 11 | 12 | 44 | 68 | 2.1 | 12.02 | 50 | 76.7 | 40 | 61.8 | 50.3 | 219.2 | 188.3 | 188.3 | NO
| NG | 38 | 39 | 64 | 70 | 1.8 | 2.59 | 50 | 76.7 | 40 | 73.7 | 40.1 | 206.3 | 220.2 | 206.3 | NO
| NG | 54 | 55 | 94 | 70 | 142.9 | 4.1 | 50 | 76.7 | 40 | 71.8 | 43.1 | 207.6 | 216.3 | 207.6 | NO
| NG | 12 | 13 | 13 | 68 | 93.2 | 2.87 | 50 | 76.7 | 40 | 73.2 | 42.2 | 205.9 | 219.9 | 205.9 | NO
| NG | 12 | 43 | 44 | 68 | 2.1 | 9.15 | 50 | 76.7 | 40 | 65.4 | 47.4 | 213.3 | 199.6 | 199.6 | NO
| NG | 39 | 64 | 64 | 70 | 1.8 | 0.06 | 50 | 76.7 | 40 | 76.6 | 40.1 | 206.3 | 220.2 | 206.3 | NO
| NG | 55 | 47 | 94 | 70 | 142.9 | 3.37 | 50 | 76.7 | 40 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 40.0% (degenerate)
| NG | 13 | 14 | 14 | 68 | 103.1 | 0.15 | 50 | 76.7 | 40 | 76.5 | 40.1 | 206.3 | 220.2 | 206.3 | NO
| NG | 43 | 44 | 44 | 68 | 2.1 | 8.82 | 50 | 76.7 | 40 | 65.8 | 47.1 | 213.5 | 200.7 | 200.7 | NO
| NG | 47 | 48 | 94 | 70 | 142.9 | 3.37 | 50 | 76.7 | 40 | 72.7 | 2026.8 | 207.4 | 77.7 | 77.7 | NO
1 | OK | 44 | 76 | 76 | 82 | 3.8 | 5.12 | 50 | 76.7 | 40 | 70.1 | 43.9 | 214.8 | 212.6 | 212.6 | YES
| NG | 48 | 49 | 94 | 70 | 142.9 | 3.37 | 50 | 76.7 | 40 | 72.7 | 42.5 | 207.4 | 218.7 | 207.4 | NO
2 | OK | 76 | 77 | 84 | 85 | 6.4 | 4.26 | 50 | 76.7 | 40 | 71.2 | 43.3 | 215.2 | 214.8 | 214.8 | YES
| NG | 76 | 80 | 90 | 86 | 6.2 | 0.86 | 50 | 76.7 | 40 | 75.6 | 40.6 | 208.6 | 220.2 | 208.6 | NO
| NG | 49 | 50 | 94 | 70 | 142.9 | 2.45 | 50 | 76.7 | 40 | 73.7 | 41.8 | 207.1 | 220.2 | 207.1 | NO
3 | ** OPTIMAL ** | 77 | 89 | 84 | 85 | 6.4 | 3.39 | 50 | 76.7 | 40 | 72.3 | 42.6 | 215.5 | 217.9 | 215.5 | YES
| NG | 77 | 92 | 92 | 84 | 43.8 | 0.87 | 50 | 76.7 | 40 | 75.5 | 40.7 | 208.7 | 220.2 | 208.7 | NO
| NG | 80 | 81 | 90 | 86 | 6.2 | 0.84 | 50 | 76.7 | 40 | 75.6 | 40.6 | 208.5 | 220.2 | 208.5 | NO
| NG | 50 | 72 | 94 | 70 | 142.9 | 2.44 | 50 | 76.7 | 40 | 73.8 | 41.8 | 207.1 | 220.2 | 207.1 | NO
4 | OK | 89 | 84 | 84 | 85 | 6.4 | 2.93 | 50 | 76.7 | 40 | 72.8 | 42.2 | 214.9 | 219.4 | 214.9 | YES
| NG | 89 | 87 | 87 | 84 | 33.8 | 0.46 | 50 | 76.7 | 40 | 76.1 | 40.4 | 207.6 | 220.2 | 207.6 | NO
| NG | 92 | 91 | 91 | 82 | 79.1 | 0.44 | 50 | 76.7 | 40 | 76.1 | 40.3 | 207.5 | 220.2 | 207.5 | NO
| NG | 81 | 78 | 90 | 86 | 6.2 | 0.69 | 50 | 76.7 | 40 | 75.8 | 40.5 | 208.1 | 220.2 | 208.1 | NO
| NG | 72 | 94 | 94 | 70 | 142.9 | 0.1 | 50 | 76.7 | 40 | 76.6 | 40.1 | 206.4 | 220.2 | 206.4 | NO
5 | OK | 84 | 82 | 82 | 85 | 18.5 | 2.93 | 50 | 76.7 | 40 | 72.8 | 42.2 | 214.9 | 219.4 | 214.9 | YES
| NG | 78 | 79 | 90 | 86 | 6.2 | 0.18 | 50 | 76.7 | 40 | 76.5 | 40.2 | 206.8 | 220.2 | 206.8 | NO
| NG | 94 | 95 | 95 | 70 | 143.8 | 0.1 | 50 | 76.7 | 40 | 76.6 | 40 | 206.4 | 220.2 | 206.4 | NO
6 | OK | 82 | 83 | 83 | 85 | 33.8 | 1.28 | 50 | 76.7 | 40 | 75 | 41 | 210.2 | 220.2 | 210.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-004254
TR_B (available) | 63-023270
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 76.7
TR_B Baseline Loading% | 40
Total Scenarios Evaluated | 88
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 77
Switch Child Node | 89
Tie Node (TR_A side) | 84
Tie Node (TR_B side) | 85
Tie Line Distance (m) | 6.4
Load Transferred (kW) | 3.39
TR_A Loading After (%) | 72.3
TR_B Loading After (%) | 42.6
Minimum Voltage (V) | 215.5