## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 22 | 21 | 6 | 8 | 7.3 | 7.27 | 50 | 81.1 | 6.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 22 | 20 | 20 | 6 | 139.4 | 13.75 | 50 | 81.1 | 6.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 21 | 0 | 6 | 8 | 7.3 | 4.46 | 50 | 81.1 | 6.3 | 64.1 | 11 | 217.5 | 227.7 | 217.5 | YES
2 | OK | 0 | 1 | 19 | 6 | 32 | 2.81 | 50 | 81.1 | 6.3 | 70.4 | 17.1 | 217.2 | 227.1 | 217.2 | YES
3 | OK | 0 | 8 | 6 | 8 | 7.3 | 1.65 | 50 | 81.1 | 6.3 | 74.8 | 11 | 215.3 | 227.7 | 215.3 | YES
4 | OK | 1 | 17 | 19 | 6 | 32 | 2.39 | 50 | 81.1 | 6.3 | 72 | 15.5 | 216.8 | 227.5 | 216.8 | YES
5 | OK | 8 | 7 | 6 | 8 | 7.3 | 1.65 | 50 | 81.1 | 6.3 | 74.8 | 11 | 215.3 | 227.7 | 215.3 | YES
6 | OK | 17 | 18 | 19 | 6 | 32 | 0.55 | 50 | 81.1 | 6.3 | 79 | 8.4 | 215.4 | 229.2 | 215.4 | YES
7 | OK | 7 | 5 | 6 | 8 | 7.3 | 1.22 | 50 | 81.1 | 6.3 | 76.5 | 11 | 215 | 227.7 | 215 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-013647
TR_B (available) | 35-012361
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.1
TR_B Baseline Loading% | 6.3
Total Scenarios Evaluated | 9
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 21
Switch Child Node | 0
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 7.3
Load Transferred (kW) | 4.46
TR_A Loading After (%) | 64.1
TR_B Loading After (%) | 11
Minimum Voltage (V) | 217.5