## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 2 | 3 | 12 | 0 | 55.5 | 9.83 | 50 | 81.1 | 56.1 | 42.8 | 80.3 | 223.4 | 202.2 | 202.2 | NO
| NG | 3 | 4 | 12 | 0 | 55.5 | 9.07 | 50 | 81.1 | 56.1 | 45.7 | 78.3 | 223.4 | 204.5 | 204.5 | NO
| NG | 4 | 9 | 12 | 0 | 55.5 | 7.61 | 50 | 81.1 | 56.1 | 51.3 | 74.5 | 223.4 | 208.4 | 208.4 | NO
| NG | 9 | 10 | 12 | 0 | 55.5 | 6.91 | 50 | 81.1 | 56.1 | 54 | 72.8 | 222.9 | 208.3 | 208.3 | NO
1 | ** OPTIMAL ** | 10 | 11 | 12 | 0 | 55.5 | 3.64 | 50 | 81.1 | 56.1 | 66.8 | 64.7 | 220.3 | 215.2 | 215.2 | YES
2 | OK | 11 | 12 | 12 | 0 | 55.5 | 3.64 | 50 | 81.1 | 56.1 | 66.8 | 64.7 | 220.3 | 215.2 | 215.2 | YES
3 | OK | 12 | 13 | 13 | 0 | 74.9 | 3.64 | 50 | 81.1 | 56.1 | 66.8 | 64.7 | 220.3 | 215.2 | 215.2 | YES
4 | OK | 13 | 14 | 14 | 0 | 95.8 | 2.27 | 50 | 81.1 | 56.1 | 72.1 | 61.4 | 220.5 | 215.1 | 215.1 | YES
5 | OK | 14 | 15 | 15 | 0 | 125.5 | 2.27 | 50 | 81.1 | 56.1 | 72.1 | 61.4 | 220.5 | 215.1 | 215.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-013647
TR_B (available) | 45-016926
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 81.1
TR_B Baseline Loading% | 56.1
Total Scenarios Evaluated | 9
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 10
Switch Child Node | 11
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 55.5
Load Transferred (kW) | 3.64
TR_A Loading After (%) | 66.8
TR_B Loading After (%) | 64.7
Minimum Voltage (V) | 215.2