## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 32 | 19 | 12 | 13 | 4.1 | 19.81 | 50 | 115.9 | 23.4 | 38.5 | 50.1 | 214.6 | 181.9 | 181.9 | NO
| NG | 19 | 29 | 12 | 13 | 4.1 | 18.47 | 50 | 115.9 | 23.4 | 43.6 | 47.8 | 213.5 | 189.6 | 189.6 | NO
| NG | 29 | 28 | 12 | 13 | 4.1 | 14.65 | 50 | 115.9 | 23.4 | 58.2 | 42 | 211 | 204.9 | 204.9 | NO
| NG | 28 | 52 | 12 | 13 | 4.1 | 13.78 | 50 | 115.9 | 23.4 | 61.6 | 40.8 | 210.3 | 207.4 | 207.4 | NO
| NG | 52 | 30 | 12 | 13 | 4.1 | 13.78 | 50 | 115.9 | 23.4 | 61.6 | 40.8 | 210.3 | 207.4 | 207.4 | NO
| NG | 30 | 27 | 12 | 13 | 4.1 | 13.78 | 50 | 115.9 | 23.4 | 61.6 | 40.8 | 210.3 | 207.4 | 207.4 | NO
| NG | 27 | 26 | 12 | 13 | 4.1 | 12.99 | 50 | 115.9 | 23.4 | 64.6 | 39.7 | 210.3 | 208.6 | 208.6 | NO
1 | ** OPTIMAL ** | 26 | 16 | 12 | 13 | 4.1 | 11.14 | 50 | 115.9 | 23.4 | 64.6 | 37.2 | 210.3 | 211 | 210.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-014410
TR_B (available) | 57-002579
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 115.9
TR_B Baseline Loading% | 23.4
Total Scenarios Evaluated | 8
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 16
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 4.1
Load Transferred (kW) | 11.14
TR_A Loading After (%) | 64.6
TR_B Loading After (%) | 37.2
Minimum Voltage (V) | 210.3