## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 47 | 46 | 38 | 89 | 212.4 | 0.93 | 50 | 81 | 60.6 | [5 empty] | NO | TR_B sim: not converged
| NG | 47 | 25 | 49 | 89 | 143.6 | 9.67 | 50 | 81 | 60.6 | [5 empty] | NO | TR_A sim: not converged
| NG | 46 | 40 | 38 | 89 | 212.4 | 0.93 | 50 | 81 | 60.6 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 60.6% (degenerate)
| NG | 25 | 26 | 49 | 89 | 143.6 | 9.67 | 50 | 81 | 60.6 |  | 93.5 | 34763905175.1 | 143.6 | 143.6 | NO
| NG | 40 | 33 | 38 | 89 | 212.4 | 0.51 | 50 | 81 | 60.6 | [5 empty] | NO | TR_B sim: not converged
| NG | 26 | 29 | 49 | 89 | 143.6 | 9.22 | 50 | 81 | 60.6 | [5 empty] | NO | TR_A sim: not converged
| NG | 29 | 28 | 49 | 89 | 143.6 | 9.22 | 50 | 81 | 60.6 | 0 | 90.9 | 5.0808e+58 | 149.6 | 149.6 | NO
| NG | 28 | 27 | 49 | 89 | 143.6 | 9.22 | 50 | 81 | 60.6 | 43.8 | 90.9 | 218.6 | 149.6 | 149.6 | NO
| NG | 27 | 39 | 49 | 89 | 143.6 | 4.92 | 50 | 81 | 60.6 | 61.5 | 73.8 | 215 | 189.3 | 189.3 | NO
| NG | 39 | 31 | 49 | 89 | 143.6 | 4.35 | 50 | 81 | 60.6 | 63.7 | 72.1 | 214.5 | 193 | 193 | NO
| NG | 31 | 30 | 49 | 89 | 143.6 | 3.94 | 50 | 81 | 60.6 | 65.3 | 70.9 | 214.2 | 195.6 | 195.6 | NO
| NG | 30 | 5 | 49 | 89 | 143.6 | 3.42 | 50 | 81 | 60.6 | 67.6 | 69.4 | 213.7 | 198.6 | 198.6 | NO
| NG | 5 | 4 | 49 | 89 | 143.6 | 3 | 50 | 81 | 60.6 | 69.2 | 68.2 | 213.4 | 201 | 201 | NO
| NG | 4 | 6 | 49 | 89 | 143.6 | 2 | 50 | 81 | 60.6 | 73.1 | 65.6 | 212.5 | 206.3 | 206.3 | NO
| NG | 6 | 11 | 49 | 89 | 143.6 | 1.74 | 50 | 81 | 60.6 | 74.1 | 64.9 | 212.3 | 207.7 | 207.7 | NO
| NG | 11 | 3 | 49 | 89 | 143.6 | 1.68 | 50 | 81 | 60.6 | 74.4 | 64.8 | 212.2 | 208 | 208 | NO
| NG | 3 | 2 | 49 | 89 | 143.6 | 1.36 | 50 | 81 | 60.6 | 75.6 | 63.9 | 212 | 209.5 | 209.5 | NO
1 | OK | 2 | 0 | 49 | 89 | 143.6 | 1.18 | 50 | 81 | 60.6 | 76.3 | 63.5 | 211.8 | 210.3 | 210.3 | YES
2 | ** OPTIMAL ** | 0 | 1 | 49 | 89 | 143.6 | 0.81 | 50 | 81 | 60.6 | 77.8 | 62.6 | 211.5 | 211.9 | 211.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-014412
TR_B (available) | 35-006129
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 81
TR_B Baseline Loading% | 60.6
Total Scenarios Evaluated | 19
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 1
Tie Node (TR_A side) | 49
Tie Node (TR_B side) | 89
Tie Line Distance (m) | 143.6
Load Transferred (kW) | 0.81
TR_A Loading After (%) | 77.8
TR_B Loading After (%) | 62.6
Minimum Voltage (V) | 211.5