## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 4 | 5 | 5 | 13 | 83.7 | 3.36 | 50 | 86.4 | 11.7 | 73.3 | 24.8 | 222 | 222 | 222 | YES
| NG | 4 | 14 | 13 | 13 | 2.1 | 19.07 | 50 | 86.4 | 11.7 | 13.1 | 84.6 | 222.9 | 216.2 | 216.2 | NO
2 | OK | 5 | 23 | 23 | 13 | 110.7 | 3.11 | 50 | 86.4 | 11.7 | 74.3 | 23.8 | 221.8 | 222.3 | 221.8 | YES
3 | OK | 14 | 13 | 13 | 13 | 2.1 | 9.35 | 50 | 86.4 | 11.7 | 13.1 | 47.4 | 222.9 | 216.3 | 216.3 | YES
4 | OK | 23 | 8 | 8 | 13 | 141.8 | 2.9 | 50 | 86.4 | 11.7 | 75.1 | 23 | 221.8 | 222.4 | 221.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-014884
TR_B (available) | 64-013711
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 86.4
TR_B Baseline Loading% | 11.7
Total Scenarios Evaluated | 5
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 4
Switch Child Node | 5
Tie Node (TR_A side) | 5
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 83.7
Load Transferred (kW) | 3.36
TR_A Loading After (%) | 73.3
TR_B Loading After (%) | 24.8
Minimum Voltage (V) | 222