## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 37 | 26 | 46 | 93 | 167.2 | 18.8 | 50 | 100.7 | 13.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 37 | 11 | 4 | 93 | 71.2 | 7.22 | 50 | 100.7 | 13.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 26 | 25 | 46 | 93 | 167.2 | 18.3 | 50 | 100.7 | 13.8 | 27.7 | 29.1 | 225.5 | 5.3 | 5.3 | NO
1 | OK | 11 | 12 | 4 | 93 | 71.2 | 7.22 | 50 | 100.7 | 13.8 | 73 | 13.8 | 213.6 | 225.7 | 213.6 | YES
| NG | 25 | 27 | 46 | 93 | 167.2 | 13.21 | 50 | 100.7 | 13.8 | 49 | 24.4 | 224 | 202.5 | 202.5 | NO
2 | OK | 12 | 8 | 4 | 93 | 71.2 | 7.22 | 50 | 100.7 | 13.8 | 73 | 13.8 | 213.6 | 225.7 | 213.6 | YES
| NG | 27 | 33 | 46 | 93 | 167.2 | 11.82 | 50 | 100.7 | 13.8 | 54.4 | 22.5 | 224 | 207.4 | 207.4 | NO
3 | OK | 33 | 30 | 46 | 93 | 167.2 | 10.66 | 50 | 100.7 | 13.8 | 58.8 | 20.9 | 223 | 211.4 | 211.4 | YES
4 | ** OPTIMAL ** | 30 | 32 | 46 | 93 | 167.2 | 7.42 | 50 | 100.7 | 13.8 | 71.3 | 18.8 | 220.1 | 217.2 | 217.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-015046
TR_B (available) | 65-004749
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 100.7
TR_B Baseline Loading% | 13.8
Total Scenarios Evaluated | 9
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 32
Tie Node (TR_A side) | 46
Tie Node (TR_B side) | 93
Tie Line Distance (m) | 167.2
Load Transferred (kW) | 7.42
TR_A Loading After (%) | 71.3
TR_B Loading After (%) | 18.8
Minimum Voltage (V) | 217.2