## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 7 | 21 | 5 | 11.4 | 9.77 | 50 | 92.2 | 34.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 7 | 36 | 21 | 5 | 11.4 | 9.08 | 50 | 92.2 | 34.8 | 56.8 | 71.3 | 215.8 | 204.6 | 204.6 | NO
| NG | 8 | 5 | 45 | 3 | 3.2 | 13.43 | 50 | 92.2 | 34.8 | 40.2 | 93.2 | 217.9 | 184.3 | 184.3 | NO
| NG | 36 | 42 | 21 | 5 | 11.4 | 9.08 | 50 | 92.2 | 34.8 | 56.8 | 71.3 | 215.8 | 204.6 | 204.6 | NO
| NG | 5 | 11 | 45 | 3 | 3.2 | 7.18 | 50 | 92.2 | 34.8 | 64.3 | 64 | 213 | 206.8 | 206.8 | NO
| NG | 42 | 43 | 21 | 5 | 11.4 | 8.99 | 50 | 92.2 | 34.8 | 56.8 | 71 | 215.8 | 204.7 | 204.7 | NO
| NG | 11 | 12 | 45 | 3 | 3.2 | 6.21 | 50 | 92.2 | 34.8 | 68.1 | 59.8 | 212.2 | 209.4 | 209.4 | NO
| NG | 43 | 40 | 21 | 5 | 11.4 | 8.84 | 50 | 92.2 | 34.8 | 57.7 | 70.3 | 215.6 | 205.1 | 205.1 | NO
| NG | 12 | 13 | 45 | 3 | 3.2 | 6.17 | 50 | 92.2 | 34.8 | 68.2 | 59.7 | 212.2 | 209.5 | 209.5 | NO
| NG | 40 | 24 | 21 | 5 | 11.4 | 8.84 | 50 | 92.2 | 34.8 | 57.7 | 70.3 | 215.6 | 205.1 | 205.1 | NO
1 | OK | 13 | 14 | 45 | 3 | 3.2 | 5.07 | 50 | 92.2 | 34.8 | 72.5 | 55.1 | 211.3 | 212.2 | 211.3 | YES
2 | ** OPTIMAL ** | 24 | 23 | 21 | 5 | 11.4 | 6.21 | 50 | 92.2 | 34.8 | 67.9 | 59.4 | 213.5 | 213.2 | 213.2 | YES
3 | OK | 23 | 25 | 21 | 5 | 11.4 | 5.5 | 50 | 92.2 | 34.8 | 70.6 | 56.5 | 212.9 | 214.6 | 212.9 | YES
4 | OK | 25 | 26 | 21 | 5 | 11.4 | 4.16 | 50 | 92.2 | 34.8 | 75.8 | 51.1 | 211.8 | 216.8 | 211.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-018347
TR_B (available) | 55-004841
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 92.2
TR_B Baseline Loading% | 34.8
Total Scenarios Evaluated | 14
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 23
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 11.4
Load Transferred (kW) | 6.21
TR_A Loading After (%) | 67.9
TR_B Loading After (%) | 59.4
Minimum Voltage (V) | 213.2