## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 74 | 7 | 10 | 10 | 30.3 | 53.62 | 50 | 80.2 | 48.9 | 40.9 | 59.6 | 222 | 186.2 | 186.2 | NO
| NG | 7 | 93 | 10 | 10 | 30.3 | 46.09 | 50 | 80.2 | 48.9 | 46.3 | 57.6 | 221.7 | 191.4 | 191.4 | NO
| NG | 93 | 25 | 10 | 10 | 30.3 | 44.48 | 50 | 80.2 | 48.9 | 47.5 | 57.6 | 221.7 | 191.4 | 191.4 | NO
| NG | 25 | 26 | 10 | 10 | 30.3 | 44.48 | 50 | 80.2 | 48.9 | 47.5 | 57.6 | 221.7 | 191.4 | 191.4 | NO
| NG | 26 | 27 | 10 | 10 | 30.3 | 42.71 | 50 | 80.2 | 48.9 | 48.7 | 56.5 | 221.7 | 194.2 | 194.2 | NO
| NG | 27 | 28 | 10 | 10 | 30.3 | 39.3 | 50 | 80.2 | 48.9 | 51.2 | 55.6 | 221.6 | 196.3 | 196.3 | NO
| NG | 28 | 29 | 10 | 10 | 30.3 | 37.46 | 50 | 80.2 | 48.9 | 52.5 | 55.6 | 221.4 | 196.3 | 196.3 | NO
| NG | 29 | 30 | 10 | 10 | 30.3 | 37.46 | 50 | 80.2 | 48.9 | 52.5 | 55.6 | 221.4 | 196.3 | 196.3 | NO
| NG | 30 | 19 | 10 | 10 | 30.3 | 36.49 | 50 | 80.2 | 48.9 | 52.6 | 55.6 | 221.4 | 196.3 | 196.3 | NO
| NG | 19 | 22 | 10 | 10 | 30.3 | 31.92 | 50 | 80.2 | 48.9 | 56.5 | 54.7 | 221.1 | 198.5 | 198.5 | NO
| NG | 19 | 75 | 79 | 10 | 86.8 | 3.24 | 50 | 80.2 | 48.9 | 77.8 | 50.6 | 215.5 | 209.7 | 209.7 | NO
| NG | 22 | 92 | 31 | 51 | 79.7 | 2.25 | 50 | 80.2 | 48.9 | 78.6 | 49.2 | 215.5 | 209.8 | 209.8 | NO
| NG | 22 | 104 | 10 | 10 | 30.3 | 29.3 | 50 | 80.2 | 48.9 | 57.2 | 54.5 | 221.1 | 199 | 199 | NO
1 | OK | 75 | 77 | 77 | 10 | 110.5 | 1.34 | 50 | 80.2 | 48.9 | 79.1 | 49.1 | 215.4 | 210.2 | 210.2 | YES
| NG | 75 | 78 | 79 | 10 | 86.8 | 1.37 | 50 | 80.2 | 48.9 | 79.2 | 49.6 | 215.2 | 210 | 210 | NO
2 | OK | 92 | 32 | 31 | 51 | 79.7 | 1.85 | 50 | 80.2 | 48.9 | 78.9 | 49 | 215.5 | 210.1 | 210.1 | YES
| NG | 104 | 98 | 10 | 10 | 30.3 | 28.52 | 50 | 80.2 | 48.9 | 57.8 | 54.5 | 221 | 199 | 199 | NO
3 | OK | 77 | 76 | 76 | 10 | 117 | 1.08 | 50 | 80.2 | 48.9 | 79.4 | 48.9 | 215.3 | 210.2 | 210.2 | YES
4 | OK | 78 | 79 | 79 | 10 | 86.8 | 0.77 | 50 | 80.2 | 48.9 | 79.6 | 48.9 | 215.6 | 210.2 | 210.2 | YES
5 | OK | 32 | 31 | 31 | 51 | 79.7 | 1.85 | 50 | 80.2 | 48.9 | 78.8 | 48.9 | 215.4 | 210.2 | 210.2 | YES
| NG | 98 | 96 | 21 | 51 | 47.9 | 27.39 | 50 | 80.2 | 48.9 | 59.8 | 63.1 | 221 | 204.2 | 204.2 | NO
6 | OK | 98 | 8 | 10 | 10 | 30.3 | 1.02 | 50 | 80.2 | 48.9 | 79.5 | 49.5 | 215 | 210.2 | 210.2 | YES
| NG | 96 | 103 | 21 | 51 | 47.9 | 27.39 | 50 | 80.2 | 48.9 | 59.8 | 63.1 | 221 | 204.2 | 204.2 | NO
7 | OK | 8 | 9 | 10 | 10 | 30.3 | 1.02 | 50 | 80.2 | 48.9 | 79.5 | 49.5 | 215 | 210.2 | 210.2 | YES
| NG | 103 | 21 | 21 | 51 | 47.9 | 27.25 | 50 | 80.2 | 48.9 | 59.9 | 63 | 220.9 | 204.2 | 204.2 | NO
| NG | 21 | 20 | 20 | 10 | 54.4 | 26.04 | 50 | 80.2 | 48.9 | 60.8 | 62.3 | 220.9 | 205.8 | 205.8 | NO
| NG | 20 | 1 | 1 | 10 | 64.4 | 21.51 | 50 | 80.2 | 48.9 | 64 | 59.9 | 220.7 | 207.4 | 207.4 | NO
| NG | 1 | 0 | 0 | 10 | 87.1 | 20.15 | 50 | 80.2 | 48.9 | 65 | 59.1 | 220.7 | 207.4 | 207.4 | NO
| NG | 0 | 3 | 2 | 22 | 91.7 | 16.99 | 50 | 80.2 | 48.9 | 67.4 | 52 | 220.5 | 204.1 | 204.1 | NO
| NG | 3 | 2 | 2 | 22 | 91.7 | 10.57 | 50 | 80.2 | 48.9 | 72.1 | 50.6 | 220.2 | 208.8 | 208.8 | NO
8 | ** OPTIMAL ** | 2 | 102 | 102 | 22 | 92.9 | 9.5 | 50 | 80.2 | 48.9 | 73 | 49.8 | 219.6 | 210.3 | 210.3 | YES
9 | OK | 102 | 5 | 5 | 22 | 98.4 | 5.94 | 50 | 80.2 | 48.9 | 75.7 | 49.8 | 216.6 | 210.3 | 210.3 | YES
10 | OK | 5 | 4 | 4 | 22 | 108.9 | 3.08 | 50 | 80.2 | 48.9 | 77.9 | 48.9 | 215.1 | 210.2 | 210.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-023340
TR_B (available) | 33-006260
TR_A Rated kVA | 160
TR_B Rated kVA | 250
TR_A Baseline Loading% | 80.2
TR_B Baseline Loading% | 48.9
Total Scenarios Evaluated | 33
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 102
Tie Node (TR_A side) | 102
Tie Node (TR_B side) | 22
Tie Line Distance (m) | 92.9
Load Transferred (kW) | 9.5
TR_A Loading After (%) | 73
TR_B Loading After (%) | 49.8
Minimum Voltage (V) | 210.3