## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 74 | 7 | 18 | 12 | 21 | 53.62 | 95 | 80.2 | 32.4 | 40.9 | 73.7 | 222 | 205.5 | 205.5 | NO
1 | OK | 74 | 72 | 42 | 12 | 101.6 | 48.71 | 95 | 80.2 | 32.4 | 45 | 44.1 | 217.7 | 212.5 | 212.5 | YES
2 | OK | 74 | 15 | 12 | 12 | 6.1 | 7.96 | 95 | 80.2 | 32.4 | 74.5 | 38.1 | 215.7 | 225.8 | 215.7 | YES
3 | OK | 7 | 6 | 18 | 12 | 21 | 6.99 | 95 | 80.2 | 32.4 | 75.2 | 37.4 | 215.4 | 225.7 | 215.4 | YES
| NG | 7 | 93 | 21 | 54 | 60.4 | 46.09 | 50 | 80.2 | 32.4 | 46.3 | 69.2 | 221.7 | 201.1 | 201.1 | NO
4 | OK | 72 | 69 | 42 | 12 | 101.6 | 47 | 95 | 80.2 | 32.4 | 46.2 | 44.1 | 217.6 | 212.5 | 212.5 | YES
5 | OK | 15 | 14 | 13 | 12 | 65.1 | 2.26 | 95 | 80.2 | 32.4 | 78.6 | 34 | 215.5 | 226 | 215.5 | YES
6 | OK | 15 | 16 | 12 | 12 | 6.1 | 2.26 | 95 | 80.2 | 32.4 | 76.9 | 34 | 215.5 | 225.9 | 215.5 | YES
7 | OK | 15 | 87 | 95 | 12 | 36.3 | 3.01 | 95 | 80.2 | 32.4 | 78.1 | 32.9 | 215.5 | 226 | 215.5 | YES
8 | OK | 6 | 37 | 18 | 12 | 21 | 6.99 | 95 | 80.2 | 32.4 | 75.2 | 37.4 | 215.5 | 225.7 | 215.5 | YES
| NG | 93 | 25 | 21 | 54 | 60.4 | 44.48 | 50 | 80.2 | 32.4 | 47.5 | 67.9 | 221.7 | 200.9 | 200.9 | NO
9 | ** OPTIMAL ** | 69 | 47 | 42 | 12 | 101.6 | 27.61 | 95 | 80.2 | 32.4 | 60.2 | 40.3 | 216.2 | 216.5 | 216.2 | YES
10 | OK | 69 | 73 | 73 | 12 | 151.9 | 19.39 | 95 | 80.2 | 32.4 | 66.1 | 46.8 | 216.6 | 215.3 | 215.3 | YES
11 | OK | 16 | 12 | 12 | 12 | 6.1 | 2.26 | 95 | 80.2 | 32.4 | 77.5 | 34 | 215.4 | 225.9 | 215.4 | YES
12 | OK | 87 | 95 | 95 | 12 | 36.3 | 2.02 | 95 | 80.2 | 32.4 | 78.8 | 32.7 | 215.3 | 226 | 215.3 | YES
13 | OK | 37 | 39 | 39 | 12 | 78.3 | 1.01 | 50 | 80.2 | 32.4 | 79.5 | 32.4 | 215.2 | 226 | 215.2 | YES
14 | OK | 37 | 36 | 18 | 12 | 21 | 2.91 | 95 | 80.2 | 32.4 | 78.1 | 34.5 | 215.4 | 225.9 | 215.4 | YES
| NG | 25 | 26 | 21 | 54 | 60.4 | 44.48 | 50 | 80.2 | 32.4 | 47.5 | 67.9 | 221.7 | 200.9 | 200.9 | NO
15 | OK | 47 | 46 | 42 | 12 | 101.6 | 17.97 | 95 | 80.2 | 32.4 | 67.2 | 38.3 | 215.6 | 218.6 | 215.6 | YES
16 | OK | 12 | 11 | 11 | 12 | 32.8 | 2.26 | 95 | 80.2 | 32.4 | 77.5 | 34 | 215.4 | 225.9 | 215.4 | YES
17 | OK | 36 | 85 | 18 | 12 | 21 | 1.63 | 95 | 80.2 | 32.4 | 79.1 | 33.5 | 215.4 | 226 | 215.4 | YES
| NG | 26 | 27 | 21 | 54 | 60.4 | 42.71 | 50 | 80.2 | 32.4 | 48.7 | 66.3 | 221.7 | 200.1 | 200.1 | NO
18 | OK | 46 | 41 | 42 | 12 | 101.6 | 17.97 | 95 | 80.2 | 32.4 | 67.2 | 38.1 | 215.6 | 218.8 | 215.6 | YES
19 | OK | 85 | 18 | 18 | 12 | 21 | 1.63 | 95 | 80.2 | 32.4 | 79.1 | 33.5 | 215.4 | 226 | 215.4 | YES
| NG | 27 | 28 | 21 | 54 | 60.4 | 39.3 | 50 | 80.2 | 32.4 | 51.2 | 63.4 | 221.6 | 201.8 | 201.8 | NO
20 | OK | 27 | 80 | 80 | 63 | 121.3 | 1.43 | 50 | 80.2 | 32.4 | 79.2 | 33.4 | 215.1 | 225.9 | 215.1 | YES
21 | OK | 41 | 40 | 42 | 12 | 101.6 | 0.8 | 95 | 80.2 | 32.4 | 79.6 | 32.7 | 215.2 | 226 | 215.2 | YES
22 | OK | 41 | 50 | 50 | 12 | 142.9 | 16.89 | 50 | 80.2 | 32.4 | 67.9 | 44.9 | 215.6 | 217.3 | 215.6 | YES
| NG | 18 | 35 | 34 | 45 | 22.3 | 0.49 | 50 | 80.2 | 32.4 | [5 empty] | NO | TR_A sim: loading 3113% (degenerate)
| NG | 28 | 29 | 21 | 54 | 60.4 | 37.46 | 50 | 80.2 | 32.4 | 52.5 | 61.9 | 221.4 | 203.6 | 203.6 | NO
23 | OK | 80 | 81 | 81 | 12 | 122 | 0.77 | 95 | 80.2 | 32.4 | 79.7 | 32.4 | 215.2 | 226 | 215.2 | YES
| NG | 40 | 43 | 42 | 12 | 101.6 | 0.52 | 95 | 80.2 | 32.4 | [5 empty] | NO | TR_A sim: loading 1273% (degenerate)
| NG | 29 | 30 | 21 | 54 | 60.4 | 37.46 | 50 | 80.2 | 32.4 | 52.5 | 61.9 | 221.4 | 203.6 | 203.6 | NO
| NG | 30 | 19 | 21 | 54 | 60.4 | 36.49 | 50 | 80.2 | 32.4 | 52.6 | 61 | 221.4 | 205.4 | 205.4 | NO
| NG | 19 | 22 | 21 | 54 | 60.4 | 31.92 | 50 | 80.2 | 32.4 | 56.5 | 56.3 | 221.1 | 209 | 209 | NO
24 | OK | 19 | 75 | 79 | 54 | 90.5 | 3.24 | 50 | 80.2 | 32.4 | 77.8 | 34.7 | 215.5 | 223.8 | 215.5 | YES
25 | OK | 22 | 92 | 31 | 54 | 69 | 2.25 | 50 | 80.2 | 32.4 | 78.6 | 32.8 | 215.5 | 226 | 215.5 | YES
| NG | 22 | 104 | 21 | 54 | 60.4 | 29.3 | 50 | 80.2 | 32.4 | 57.2 | 54.5 | 221.1 | 209.2 | 209.2 | NO
26 | OK | 75 | 77 | 77 | 51 | 98.1 | 1.34 | 50 | 80.2 | 32.4 | 79.1 | 32.4 | 215.4 | 226 | 215.4 | YES
27 | OK | 75 | 78 | 79 | 54 | 90.5 | 1.37 | 50 | 80.2 | 32.4 | 79.2 | 33.4 | 215.2 | 225.2 | 215.2 | YES
28 | OK | 92 | 32 | 31 | 54 | 69 | 1.85 | 50 | 80.2 | 32.4 | 78.9 | 32.5 | 215.5 | 226 | 215.5 | YES
| NG | 104 | 98 | 21 | 54 | 60.4 | 28.52 | 50 | 80.2 | 32.4 | 57.8 | 54.5 | 221 | 209.1 | 209.1 | NO
29 | OK | 77 | 76 | 76 | 51 | 99.5 | 1.08 | 50 | 80.2 | 32.4 | 79.4 | 32.4 | 215.3 | 226 | 215.3 | YES
30 | OK | 78 | 79 | 79 | 54 | 90.5 | 0.77 | 50 | 80.2 | 32.4 | 79.6 | 32.4 | 215.6 | 226 | 215.6 | YES
31 | OK | 32 | 31 | 31 | 54 | 69 | 1.85 | 50 | 80.2 | 32.4 | 78.8 | 32.4 | 215.4 | 226 | 215.4 | YES
| NG | 98 | 96 | 21 | 54 | 60.4 | 27.39 | 50 | 80.2 | 32.4 | 59.8 | 53.6 | 221 | 209 | 209 | NO
32 | OK | 98 | 8 | 8 | 54 | 77.6 | 1.02 | 50 | 80.2 | 32.4 | 79.5 | 33.1 | 215 | 224.4 | 215 | YES
| NG | 96 | 103 | 21 | 54 | 60.4 | 27.39 | 50 | 80.2 | 32.4 | 59.8 | 53.6 | 221 | 209 | 209 | NO
33 | OK | 8 | 9 | 9 | 54 | 79.7 | 1.02 | 50 | 80.2 | 32.4 | 79.5 | 33.1 | 215 | 224.4 | 215 | YES
| NG | 103 | 21 | 21 | 54 | 60.4 | 27.25 | 50 | 80.2 | 32.4 | 59.9 | 53.5 | 220.9 | 209.2 | 209.2 | NO
| NG | 21 | 20 | 20 | 54 | 104.6 | 26.04 | 50 | 80.2 | 32.4 | 60.8 | 52.5 | 220.9 | 209.8 | 209.8 | NO
34 | OK | 20 | 1 | 1 | 54 | 120.5 | 21.51 | 50 | 80.2 | 32.4 | 64 | 48.9 | 220.7 | 212.4 | 212.4 | YES
35 | OK | 1 | 0 | 0 | 54 | 149.2 | 20.15 | 50 | 80.2 | 32.4 | 65 | 47.8 | 220.7 | 211.8 | 211.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-023340
TR_B (available) | 42-004819
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.2
TR_B Baseline Loading% | 32.4
Total Scenarios Evaluated | 53
Feasible Scenarios | 35
--- Optimal Solution ---
Switch Parent Node | 69
Switch Child Node | 47
Tie Node (TR_A side) | 42
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 101.6
Load Transferred (kW) | 27.61
TR_A Loading After (%) | 60.2
TR_B Loading After (%) | 40.3
Minimum Voltage (V) | 216.2