## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 74 | 7 | 81 | 26 | 138.1 | 53.62 | 50 | 80.2 | 18.1 | 40.9 | 61.4 | 222 | 196.9 | 196.9 | NO
| NG | 74 | 72 | 24 | 26 | 16.4 | 48.71 | 50 | 80.2 | 18.1 | 45 | 55.6 | 217.7 | 205.5 | 205.5 | NO
| NG | 7 | 93 | 81 | 26 | 138.1 | 46.09 | 50 | 80.2 | 18.1 | 46.3 | 54.9 | 221.7 | 199.2 | 199.2 | NO
| NG | 72 | 69 | 24 | 26 | 16.4 | 47 | 50 | 80.2 | 18.1 | 46.2 | 54.2 | 217.6 | 205.9 | 205.9 | NO
| NG | 93 | 25 | 81 | 26 | 138.1 | 44.48 | 50 | 80.2 | 18.1 | 47.5 | 53.5 | 221.7 | 198.9 | 198.9 | NO
1 | OK | 69 | 47 | 24 | 26 | 16.4 | 27.61 | 50 | 80.2 | 18.1 | 60.2 | 38.8 | 216.2 | 213.3 | 213.3 | YES
2 | OK | 69 | 73 | 70 | 26 | 23.5 | 19.39 | 50 | 80.2 | 18.1 | 66.1 | 32.6 | 216.6 | 215.5 | 215.5 | YES
| NG | 25 | 26 | 81 | 26 | 138.1 | 44.48 | 50 | 80.2 | 18.1 | 47.5 | 53.5 | 221.7 | 198.9 | 198.9 | NO
3 | OK | 47 | 46 | 46 | 26 | 111.7 | 17.97 | 50 | 80.2 | 18.1 | 67.2 | 31.6 | 215.6 | 213.8 | 213.8 | YES
4 | OK | 47 | 48 | 24 | 26 | 16.4 | 9.64 | 50 | 80.2 | 18.1 | 73.2 | 25.2 | 215.8 | 224.3 | 215.8 | YES
5 | OK | 73 | 100 | 70 | 26 | 23.5 | 18.63 | 50 | 80.2 | 18.1 | 66.7 | 32 | 216.6 | 215.4 | 215.4 | YES
| NG | 26 | 27 | 81 | 26 | 138.1 | 42.71 | 50 | 80.2 | 18.1 | 48.7 | 52 | 221.7 | 198.1 | 198.1 | NO
6 | OK | 46 | 41 | 41 | 26 | 114.1 | 17.97 | 50 | 80.2 | 18.1 | 67.2 | 31.4 | 215.6 | 214.2 | 214.2 | YES
7 | OK | 48 | 84 | 24 | 26 | 16.4 | 8.24 | 50 | 80.2 | 18.1 | 74.3 | 22.5 | 215.7 | 224.5 | 215.7 | YES
8 | OK | 100 | 101 | 70 | 26 | 23.5 | 15.44 | 50 | 80.2 | 18.1 | 69 | 29.2 | 216.4 | 216.8 | 216.4 | YES
9 | OK | 27 | 80 | 81 | 26 | 138.1 | 1.43 | 50 | 80.2 | 18.1 | 79.2 | 19.2 | 215.1 | 225.2 | 215.1 | YES
10 | OK | 41 | 40 | 40 | 26 | 134.4 | 0.8 | 50 | 80.2 | 18.1 | 79.6 | 18.7 | 215.2 | 225.2 | 215.2 | YES
11 | OK | 41 | 50 | 50 | 26 | 116.2 | 16.89 | 50 | 80.2 | 18.1 | 67.9 | 30.7 | 215.6 | 215.3 | 215.3 | YES
12 | OK | 84 | 23 | 24 | 26 | 16.4 | 5.96 | 50 | 80.2 | 18.1 | 75.9 | 22.5 | 215.7 | 224.5 | 215.7 | YES
13 | OK | 101 | 71 | 70 | 26 | 23.5 | 13.91 | 50 | 80.2 | 18.1 | 70.1 | 28.5 | 216.4 | 216.6 | 216.4 | YES
14 | OK | 80 | 81 | 81 | 26 | 138.1 | 0.77 | 50 | 80.2 | 18.1 | 79.7 | 18.1 | 215.2 | 225.4 | 215.2 | YES
| NG | 40 | 43 | 43 | 26 | 141.6 | 0.52 | 50 | 80.2 | 18.1 | [5 empty] | NO | TR_A sim: loading 1273% (degenerate)
15 | OK | 50 | 51 | 53 | 26 | 120.6 | 16.89 | 50 | 80.2 | 18.1 | 67.9 | 23.6 | 215.6 | 216.9 | 215.6 | YES
16 | OK | 23 | 49 | 49 | 26 | 32.9 | 5.95 | 50 | 80.2 | 18.1 | 75.9 | 22.5 | 215.7 | 224.4 | 215.7 | YES
17 | OK | 71 | 91 | 91 | 26 | 41.8 | 13.89 | 50 | 80.2 | 18.1 | 70.1 | 28.5 | 216.4 | 216.6 | 216.4 | YES
18 | OK | 51 | 60 | 53 | 26 | 120.6 | 11.63 | 50 | 80.2 | 18.1 | 71.7 | 23.6 | 215.5 | 216.9 | 215.5 | YES
19 | OK | 49 | 17 | 17 | 26 | 59.8 | 4.87 | 50 | 80.2 | 18.1 | 76.7 | 21.7 | 215.6 | 225 | 215.6 | YES
20 | ** OPTIMAL ** | 91 | 64 | 67 | 26 | 76.4 | 13.52 | 50 | 80.2 | 18.1 | 70.3 | 20.3 | 216.4 | 223.7 | 216.4 | YES
21 | OK | 60 | 52 | 53 | 26 | 120.6 | 6.86 | 50 | 80.2 | 18.1 | 74.4 | 21.8 | 215.5 | 220.1 | 215.5 | YES
22 | OK | 60 | 61 | 61 | 26 | 137.6 | 3.68 | 50 | 80.2 | 18.1 | 77.5 | 20.8 | 215.2 | 224 | 215.2 | YES
| NG | 64 | 63 | 63 | 26 | 79 | 11.66 | 50 | 80.2 | 18.1 | 71.2 | 2569.4 | 216.4 | 20 | 20 | NO
| NG | 64 | 66 | 66 | 26 | 82.4 | 1.35 | 50 | 80.2 | 18.1 | 0 | 18.6 | 197 | 225.2 | 197 | NO
23 | OK | 64 | 67 | 67 | 26 | 76.4 | 0.51 | 50 | 80.2 | 18.1 | 79.9 | 18.5 | 215.2 | 225.2 | 215.2 | YES
24 | OK | 52 | 33 | 53 | 26 | 120.6 | 6.02 | 50 | 80.2 | 18.1 | 75.8 | 21.8 | 215.3 | 220.1 | 215.3 | YES
25 | OK | 63 | 62 | 62 | 26 | 118.1 | 11.16 | 50 | 80.2 | 18.1 | 72 | 26.5 | 216.3 | 217.3 | 216.3 | YES
26 | OK | 33 | 53 | 53 | 26 | 120.6 | 1.15 | 50 | 80.2 | 18.1 | 79.4 | 19 | 215.2 | 225.1 | 215.2 | YES
27 | OK | 33 | 90 | 58 | 26 | 139.8 | 4.45 | 50 | 80.2 | 18.1 | 77 | 20.6 | 215.3 | 222.5 | 215.3 | YES
28 | OK | 90 | 56 | 58 | 26 | 139.8 | 3.42 | 50 | 80.2 | 18.1 | 77.7 | 20.6 | 215.2 | 222.5 | 215.2 | YES
29 | OK | 56 | 88 | 58 | 26 | 139.8 | 3.3 | 50 | 80.2 | 18.1 | 77.8 | 20.6 | 215.2 | 222.5 | 215.2 | YES
30 | OK | 88 | 89 | 58 | 26 | 139.8 | 1.26 | 50 | 80.2 | 18.1 | 79.3 | 19.1 | 215.2 | 225 | 215.2 | YES
31 | OK | 89 | 57 | 58 | 26 | 139.8 | 0.9 | 50 | 80.2 | 18.1 | 79.6 | 18.8 | 215.2 | 225.1 | 215.2 | YES
32 | OK | 57 | 58 | 58 | 26 | 139.8 | 0.57 | 50 | 80.2 | 18.1 | 79.8 | 18.6 | 215.2 | 225.2 | 215.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-023340
TR_B (available) | 44-000132
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.2
TR_B Baseline Loading% | 18.1
Total Scenarios Evaluated | 42
Feasible Scenarios | 32
--- Optimal Solution ---
Switch Parent Node | 91
Switch Child Node | 64
Tie Node (TR_A side) | 67
Tie Node (TR_B side) | 26
Tie Line Distance (m) | 76.4
Load Transferred (kW) | 13.52
TR_A Loading After (%) | 70.3
TR_B Loading After (%) | 20.3
Minimum Voltage (V) | 216.4