## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 74 | 7 | 4 | 19 | 18.8 | 53.62 | 50 | 80.2 | 33.1 | 40.9 | 76.8 | 222 | 191.6 | 191.6 | NO
1 | OK | 74 | 72 | 70 | 30 | 0.8 | 48.71 | 95 | 80.2 | 33.1 | 45 | 69.6 | 217.7 | 213.9 | 213.9 | YES
2 | OK | 74 | 15 | 15 | 28 | 144.3 | 7.96 | 50 | 80.2 | 33.1 | 74.5 | 34.4 | 215.7 | 226.1 | 215.7 | YES
3 | OK | 7 | 6 | 6 | 28 | 142.2 | 6.99 | 50 | 80.2 | 33.1 | 75.2 | 35 | 215.4 | 225.1 | 215.4 | YES
| NG | 7 | 93 | 4 | 19 | 18.8 | 46.09 | 50 | 80.2 | 33.1 | 46.3 | 69.7 | 221.7 | 201.4 | 201.4 | NO
4 | OK | 72 | 69 | 70 | 30 | 0.8 | 47 | 95 | 80.2 | 33.1 | 46.2 | 68.2 | 217.6 | 213.8 | 213.8 | YES
5 | OK | 15 | 14 | 14 | 28 | 149.2 | 2.26 | 50 | 80.2 | 33.1 | 78.6 | 33.1 | 215.5 | 226.3 | 215.5 | YES
| NG | 93 | 25 | 4 | 19 | 18.8 | 44.48 | 50 | 80.2 | 33.1 | 47.5 | 68.3 | 221.7 | 200.1 | 200.1 | NO
6 | OK | 69 | 47 | 24 | 30 | 22.5 | 27.61 | 95 | 80.2 | 33.1 | 60.2 | 53.5 | 216.2 | 216 | 216 | YES
7 | OK | 69 | 73 | 70 | 30 | 0.8 | 19.39 | 95 | 80.2 | 33.1 | 66.1 | 47.3 | 216.6 | 218.3 | 216.6 | YES
| NG | 25 | 26 | 4 | 19 | 18.8 | 44.48 | 50 | 80.2 | 33.1 | 47.5 | 68.3 | 221.7 | 200.1 | 200.1 | NO
8 | OK | 47 | 46 | 46 | 30 | 100.4 | 17.97 | 95 | 80.2 | 33.1 | 67.2 | 46.3 | 215.6 | 217.4 | 215.6 | YES
9 | OK | 47 | 48 | 24 | 30 | 22.5 | 9.64 | 95 | 80.2 | 33.1 | 73.2 | 40.1 | 215.8 | 224.5 | 215.8 | YES
10 | OK | 73 | 100 | 70 | 30 | 0.8 | 18.63 | 95 | 80.2 | 33.1 | 66.7 | 46.8 | 216.6 | 218.3 | 216.6 | YES
| NG | 26 | 27 | 4 | 19 | 18.8 | 42.71 | 50 | 80.2 | 33.1 | 48.7 | 66.7 | 221.7 | 200 | 200 | NO
11 | OK | 46 | 41 | 41 | 30 | 102.6 | 17.97 | 95 | 80.2 | 33.1 | 67.2 | 46.1 | 215.6 | 217.7 | 215.6 | YES
12 | OK | 48 | 84 | 24 | 30 | 22.5 | 8.24 | 95 | 80.2 | 33.1 | 74.3 | 37.4 | 215.7 | 224.5 | 215.7 | YES
13 | OK | 100 | 101 | 70 | 30 | 0.8 | 15.44 | 95 | 80.2 | 33.1 | 69 | 44 | 216.4 | 219.1 | 216.4 | YES
| NG | 27 | 28 | 4 | 19 | 18.8 | 39.3 | 50 | 80.2 | 33.1 | 51.2 | 63.7 | 221.6 | 202.9 | 202.9 | NO
14 | OK | 27 | 80 | 81 | 28 | 93 | 1.43 | 50 | 80.2 | 33.1 | 79.2 | 33.6 | 215.1 | 226.3 | 215.1 | YES
15 | OK | 41 | 40 | 40 | 30 | 121.5 | 0.8 | 95 | 80.2 | 33.1 | 79.6 | 33.6 | 215.2 | 226.3 | 215.2 | YES
16 | OK | 41 | 50 | 50 | 30 | 107.3 | 16.89 | 50 | 80.2 | 33.1 | 67.9 | 45.5 | 215.6 | 217.6 | 215.6 | YES
17 | OK | 84 | 23 | 24 | 30 | 22.5 | 5.96 | 95 | 80.2 | 33.1 | 75.9 | 37.4 | 215.7 | 224.5 | 215.7 | YES
18 | OK | 101 | 71 | 70 | 30 | 0.8 | 13.91 | 95 | 80.2 | 33.1 | 70.1 | 43.3 | 216.4 | 218.9 | 216.4 | YES
| NG | 28 | 29 | 4 | 19 | 18.8 | 37.46 | 50 | 80.2 | 33.1 | 52.5 | 62.1 | 221.4 | 205.7 | 205.7 | NO
19 | OK | 80 | 81 | 81 | 28 | 93 | 0.77 | 50 | 80.2 | 33.1 | 79.7 | 33.1 | 215.2 | 226.3 | 215.2 | YES
| NG | 40 | 43 | 43 | 30 | 128.5 | 0.52 | 95 | 80.2 | 33.1 | [5 empty] | NO | TR_A sim: loading 1273% (degenerate)
20 | OK | 50 | 51 | 51 | 30 | 117.4 | 16.89 | 50 | 80.2 | 33.1 | 67.9 | 45.5 | 215.6 | 217.9 | 215.6 | YES
21 | OK | 23 | 49 | 49 | 30 | 32.6 | 5.95 | 50 | 80.2 | 33.1 | 75.9 | 37.4 | 215.7 | 224.5 | 215.7 | YES
22 | OK | 71 | 91 | 68 | 28 | 15.7 | 13.89 | 50 | 80.2 | 33.1 | 70.1 | 43.7 | 216.4 | 214 | 214 | YES
| NG | 29 | 30 | 4 | 19 | 18.8 | 37.46 | 50 | 80.2 | 33.1 | 52.5 | 62.1 | 221.4 | 205.7 | 205.7 | NO
23 | OK | 51 | 60 | 53 | 30 | 127.1 | 11.63 | 50 | 80.2 | 33.1 | 71.7 | 38.4 | 215.5 | 219 | 215.5 | YES
24 | OK | 49 | 17 | 17 | 30 | 74.8 | 4.87 | 50 | 80.2 | 33.1 | 76.7 | 36.6 | 215.6 | 225 | 215.6 | YES
25 | OK | 91 | 64 | 68 | 28 | 15.7 | 13.52 | 50 | 80.2 | 33.1 | 70.3 | 43.4 | 216.4 | 214.4 | 214.4 | YES
| NG | 30 | 19 | 4 | 19 | 18.8 | 36.49 | 50 | 80.2 | 33.1 | 52.6 | 61.3 | 221.4 | 208.5 | 208.5 | NO
26 | OK | 60 | 52 | 53 | 30 | 127.1 | 6.86 | 50 | 80.2 | 33.1 | 74.4 | 36.7 | 215.5 | 221.7 | 215.5 | YES
27 | OK | 60 | 61 | 61 | 30 | 135.3 | 3.68 | 50 | 80.2 | 33.1 | 77.5 | 35.7 | 215.2 | 225 | 215.2 | YES
| NG | 64 | 63 | 63 | 28 | 25.8 | 11.66 | 50 | 80.2 | 33.1 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 33.1% (degenerate)
| NG | 64 | 66 | 66 | 28 | 26.4 | 1.35 | 50 | 80.2 | 33.1 | 0 | 33.5 | 194.3 | 226.3 | 194.3 | NO
28 | OK | 64 | 67 | 68 | 28 | 15.7 | 0.51 | 50 | 80.2 | 33.1 | 79.9 | 33.4 | 215.2 | 226.3 | 215.2 | YES
29 | OK | 19 | 22 | 4 | 19 | 18.8 | 31.92 | 50 | 80.2 | 33.1 | 56.5 | 56.5 | 221.1 | 211.2 | 211.2 | YES
30 | OK | 19 | 75 | 83 | 28 | 94.5 | 3.24 | 50 | 80.2 | 33.1 | 77.8 | 35.4 | 215.5 | 224.7 | 215.5 | YES
31 | OK | 52 | 33 | 53 | 30 | 127.1 | 6.02 | 50 | 80.2 | 33.1 | 75.8 | 36.7 | 215.3 | 221.7 | 215.3 | YES
32 | OK | 63 | 62 | 62 | 28 | 44.4 | 11.16 | 50 | 80.2 | 33.1 | 72 | 33.9 | 216.3 | 226.3 | 216.3 | YES
33 | OK | 22 | 104 | 4 | 19 | 18.8 | 29.3 | 50 | 80.2 | 33.1 | 57.2 | 54.8 | 221.1 | 211.3 | 211.3 | YES
34 | OK | 75 | 77 | 76 | 28 | 117.9 | 1.34 | 50 | 80.2 | 33.1 | 79.1 | 33.1 | 215.4 | 226.3 | 215.4 | YES
35 | OK | 75 | 78 | 78 | 28 | 132.8 | 1.37 | 50 | 80.2 | 33.1 | 79.2 | 33.5 | 215.2 | 226.3 | 215.2 | YES
36 | OK | 33 | 53 | 53 | 30 | 127.1 | 1.15 | 50 | 80.2 | 33.1 | 79.4 | 33.9 | 215.2 | 226.3 | 215.2 | YES
37 | OK | 104 | 98 | 4 | 19 | 18.8 | 28.52 | 50 | 80.2 | 33.1 | 57.8 | 54.7 | 221 | 211.3 | 211.3 | YES
38 | OK | 77 | 76 | 76 | 28 | 117.9 | 1.08 | 50 | 80.2 | 33.1 | 79.4 | 33.1 | 215.3 | 226.3 | 215.3 | YES
39 | OK | 78 | 79 | 79 | 28 | 139.5 | 0.77 | 50 | 80.2 | 33.1 | 79.6 | 33.1 | 215.6 | 226.3 | 215.6 | YES
40 | OK | 98 | 96 | 4 | 19 | 18.8 | 27.39 | 50 | 80.2 | 33.1 | 59.8 | 53.8 | 221 | 213.8 | 213.8 | YES
41 | OK | 96 | 103 | 4 | 19 | 18.8 | 27.39 | 50 | 80.2 | 33.1 | 59.8 | 53.8 | 221 | 213.8 | 213.8 | YES
42 | OK | 103 | 21 | 4 | 19 | 18.8 | 27.25 | 50 | 80.2 | 33.1 | 59.9 | 53.7 | 220.9 | 214.2 | 214.2 | YES
43 | OK | 21 | 20 | 4 | 19 | 18.8 | 26.04 | 50 | 80.2 | 33.1 | 60.8 | 52.8 | 220.9 | 213.9 | 213.9 | YES
44 | OK | 20 | 1 | 4 | 19 | 18.8 | 21.51 | 50 | 80.2 | 33.1 | 64 | 49.2 | 220.7 | 216.2 | 216.2 | YES
45 | OK | 1 | 0 | 4 | 19 | 18.8 | 20.15 | 50 | 80.2 | 33.1 | 65 | 48.1 | 220.7 | 217.1 | 217.1 | YES
46 | OK | 0 | 3 | 4 | 19 | 18.8 | 16.99 | 50 | 80.2 | 33.1 | 67.4 | 45.7 | 220.5 | 219.3 | 219.3 | YES
47 | ** OPTIMAL ** | 3 | 2 | 4 | 19 | 18.8 | 10.57 | 50 | 80.2 | 33.1 | 72.1 | 40.8 | 220.2 | 222.6 | 220.2 | YES
48 | OK | 2 | 102 | 4 | 19 | 18.8 | 9.5 | 50 | 80.2 | 33.1 | 73 | 38 | 219.6 | 225.1 | 219.6 | YES
49 | OK | 102 | 5 | 4 | 19 | 18.8 | 5.94 | 50 | 80.2 | 33.1 | 75.7 | 37.4 | 216.6 | 225.1 | 216.6 | YES
50 | OK | 5 | 4 | 4 | 19 | 18.8 | 3.08 | 50 | 80.2 | 33.1 | 77.9 | 35.3 | 215.1 | 224.7 | 215.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-023340
TR_B (available) | 44-000171
TR_A Rated kVA | 160
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.2
TR_B Baseline Loading% | 33.1
Total Scenarios Evaluated | 62
Feasible Scenarios | 50
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 2
Tie Node (TR_A side) | 4
Tie Node (TR_B side) | 19
Tie Line Distance (m) | 18.8
Load Transferred (kW) | 10.57
TR_A Loading After (%) | 72.1
TR_B Loading After (%) | 40.8
Minimum Voltage (V) | 220.2