## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 47 | 48 | 17 | 7 | 47.6 | 9.64 | 50 | 80.2 | 48.9 | 73.2 | 65.7 | 215.8 | 218.7 | 215.8 | YES
2 | OK | 48 | 84 | 17 | 7 | 47.6 | 8.24 | 50 | 80.2 | 48.9 | 74.3 | 62.9 | 215.7 | 220 | 215.7 | YES
| NG | 100 | 101 | 70 | 8 | 67.6 | 15.44 | 50 | 80.2 | 48.9 | 69 | 84.9 | 216.4 | 207.6 | 207.6 | NO
3 | OK | 84 | 23 | 17 | 7 | 47.6 | 5.96 | 50 | 80.2 | 48.9 | 75.9 | 62.9 | 215.7 | 220 | 215.7 | YES
| NG | 101 | 71 | 70 | 8 | 67.6 | 13.91 | 50 | 80.2 | 48.9 | 70.1 | 82.5 | 216.4 | 207.3 | 207.3 | NO
4 | OK | 23 | 49 | 17 | 7 | 47.6 | 5.95 | 50 | 80.2 | 48.9 | 75.9 | 62.9 | 215.7 | 220 | 215.7 | YES
| NG | 71 | 91 | 91 | 8 | 82.3 | 13.89 | 50 | 80.2 | 48.9 | 70.1 | 82.5 | 216.4 | 207.5 | 207.5 | NO
5 | OK | 51 | 60 | 57 | 12 | 55 | 11.63 | 50 | 80.2 | 48.9 | 71.7 | 66 | 215.5 | 215 | 215 | YES
6 | OK | 49 | 17 | 17 | 7 | 47.6 | 4.87 | 50 | 80.2 | 48.9 | 76.7 | 60.3 | 215.6 | 220.9 | 215.6 | YES
7 | ** OPTIMAL ** | 91 | 64 | 67 | 8 | 120.6 | 13.52 | 50 | 80.2 | 48.9 | 70.3 | 56 | 216.4 | 220.7 | 216.4 | YES
8 | OK | 60 | 52 | 57 | 12 | 55 | 6.86 | 50 | 80.2 | 48.9 | 74.4 | 60.4 | 215.5 | 219.2 | 215.5 | YES
9 | OK | 60 | 61 | 61 | 13 | 128.7 | 3.68 | 50 | 80.2 | 48.9 | 77.5 | 57.5 | 215.2 | 222.2 | 215.2 | YES
| NG | 64 | 63 | 63 | 8 | 123 | 11.66 | 50 | 80.2 | 48.9 | 71.2 | 1259.4 | 216.4 | 20 | 20 | NO
| NG | 64 | 66 | 66 | 8 | 126.4 | 1.35 | 50 | 80.2 | 48.9 | 0 | 50.4 | 194.3 | 225.1 | 194.3 | NO
10 | OK | 64 | 67 | 67 | 8 | 120.6 | 0.51 | 50 | 80.2 | 48.9 | 79.9 | 50.1 | 215.2 | 225.3 | 215.2 | YES
11 | OK | 52 | 33 | 57 | 12 | 55 | 6.02 | 50 | 80.2 | 48.9 | 75.8 | 60.4 | 215.3 | 219.2 | 215.3 | YES
12 | OK | 61 | 59 | 59 | 13 | 149.3 | 2.45 | 50 | 80.2 | 48.9 | 78.4 | 54.6 | 215.2 | 224.2 | 215.2 | YES
13 | OK | 33 | 53 | 53 | 13 | 80.3 | 1.15 | 50 | 80.2 | 48.9 | 79.4 | 51.6 | 215.2 | 224.5 | 215.2 | YES
14 | OK | 33 | 55 | 55 | 13 | 115.5 | 0.41 | 50 | 80.2 | 48.9 | 79.9 | 49.9 | 215.2 | 225.5 | 215.2 | YES
15 | OK | 33 | 90 | 57 | 12 | 55 | 4.45 | 50 | 80.2 | 48.9 | 77 | 56.6 | 215.3 | 221.8 | 215.3 | YES
16 | OK | 90 | 56 | 57 | 12 | 55 | 3.42 | 50 | 80.2 | 48.9 | 77.7 | 56.6 | 215.2 | 221.8 | 215.2 | YES
17 | OK | 56 | 88 | 57 | 12 | 55 | 3.3 | 50 | 80.2 | 48.9 | 77.8 | 56.6 | 215.2 | 221.8 | 215.2 | YES
18 | OK | 88 | 89 | 57 | 12 | 55 | 1.26 | 50 | 80.2 | 48.9 | 79.3 | 51.9 | 215.2 | 224.6 | 215.2 | YES
19 | OK | 89 | 57 | 57 | 12 | 55 | 0.9 | 50 | 80.2 | 48.9 | 79.6 | 51 | 215.2 | 225 | 215.2 | YES
20 | OK | 57 | 58 | 58 | 13 | 59.8 | 0.57 | 50 | 80.2 | 48.9 | 79.8 | 50.3 | 215.2 | 225.4 | 215.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-023340
TR_B (available) | 62-001509
TR_A Rated kVA | 160
TR_B Rated kVA | 50
TR_A Baseline Loading% | 80.2
TR_B Baseline Loading% | 48.9
Total Scenarios Evaluated | 25
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 91
Switch Child Node | 64
Tie Node (TR_A side) | 67
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 120.6
Load Transferred (kW) | 13.52
TR_A Loading After (%) | 70.3
TR_B Loading After (%) | 56
Minimum Voltage (V) | 216.4