## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 17 | 29 | 7 | 128.7 | 12.04 | 50 | 87.3 | 35.8 | 35.7 | 85.4 | 221.1 | 199.4 | 199.4 | NO
| NG | 17 | 24 | 29 | 7 | 128.7 | 11.88 | 50 | 87.3 | 35.8 | 36.3 | 84.7 | 221 | 199.8 | 199.8 | NO
| NG | 24 | 14 | 29 | 7 | 128.7 | 10.3 | 50 | 87.3 | 35.8 | 42.5 | 77.8 | 219 | 203.6 | 203.6 | NO
| NG | 14 | 15 | 29 | 7 | 128.7 | 8.99 | 50 | 87.3 | 35.8 | 47.7 | 72.1 | 216.1 | 206.2 | 206.2 | NO
| NG | 15 | 18 | 29 | 7 | 128.7 | 8.98 | 50 | 87.3 | 35.8 | 47.8 | 72.1 | 216 | 206.2 | 206.2 | NO
1 | ** OPTIMAL ** | 18 | 27 | 29 | 7 | 128.7 | 8.98 | 50 | 87.3 | 35.8 | 47.8 | 42.9 | 216 | 219.3 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-024716
TR_B (available) | 57-001509
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 87.3
TR_B Baseline Loading% | 35.8
Total Scenarios Evaluated | 6
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 18
Switch Child Node | 27
Tie Node (TR_A side) | 29
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 128.7
Load Transferred (kW) | 8.98
TR_A Loading After (%) | 47.8
TR_B Loading After (%) | 42.9
Minimum Voltage (V) | 216