## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 21 | 29 | 29 | 5 | 48.6 | 15.98 | 50 | 93.7 | 25.7 | 31.3 | 88.6 | 224 | 205.1 | 205.1 | NO
| NG | 29 | 6 | 6 | 5 | 67.6 | 15.98 | 50 | 93.7 | 25.7 | 31.3 | 88.6 | 224 | 205 | 205 | NO
| NG | 6 | 7 | 39 | 5 | 85.3 | 12.87 | 50 | 93.7 | 25.7 | 43.2 | 76.2 | 221.5 | 208.5 | 208.5 | NO
1 | OK | 7 | 8 | 8 | 5 | 119.3 | 9.88 | 50 | 93.7 | 25.7 | 54.8 | 64.3 | 219 | 212.4 | 212.4 | YES
2 | ** OPTIMAL ** | 8 | 22 | 22 | 5 | 124.1 | 7.65 | 50 | 93.7 | 25.7 | 63.4 | 55.5 | 216 | 215.3 | 215.3 | YES
3 | OK | 22 | 9 | 9 | 5 | 127.3 | 6.34 | 50 | 93.7 | 25.7 | 68.5 | 50.3 | 214.5 | 216.9 | 214.5 | YES
4 | OK | 9 | 10 | 10 | 5 | 139.3 | 5.92 | 50 | 93.7 | 25.7 | 70.2 | 48.7 | 214.1 | 217.5 | 214.1 | YES
5 | OK | 10 | 25 | 25 | 5 | 148.3 | 5.92 | 50 | 93.7 | 25.7 | 70.2 | 48.7 | 214.1 | 217.5 | 214.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-024732
TR_B (available) | 56-004005
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 93.7
TR_B Baseline Loading% | 25.7
Total Scenarios Evaluated | 8
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 22
Tie Node (TR_A side) | 22
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 124.1
Load Transferred (kW) | 7.65
TR_A Loading After (%) | 63.4
TR_B Loading After (%) | 55.5
Minimum Voltage (V) | 215.3