## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 0 | 0 | 9 | 18.2 | 10.86 | 50 | 83.9 | 27.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 1 | 2 | 4 | 11 | 3.7 | 10.91 | 50 | 83.9 | 27.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 0 | 25 | 11 | 57 | 33.4 | 9.82 | 50 | 83.9 | 27.9 | 46 | 35.3 | 221.3 | 213.4 | 213.4 | YES
2 | OK | 2 | 3 | 4 | 11 | 3.7 | 9.22 | 50 | 83.9 | 27.9 | 48.2 | 38.7 | 222.8 | 223.2 | 222.8 | YES
3 | OK | 25 | 24 | 11 | 57 | 33.4 | 9.43 | 50 | 83.9 | 27.9 | 47.5 | 34.8 | 221.3 | 214.3 | 214.3 | YES
4 | ** OPTIMAL ** | 3 | 4 | 4 | 11 | 3.7 | 8.8 | 50 | 83.9 | 27.9 | 49.8 | 38.2 | 222.8 | 223.2 | 222.8 | YES
5 | OK | 24 | 10 | 11 | 57 | 33.4 | 2.32 | 50 | 83.9 | 27.9 | 74.9 | 30.7 | 218.4 | 222.4 | 218.4 | YES
6 | OK | 24 | 26 | 28 | 17 | 44.5 | 3.84 | 50 | 83.9 | 27.9 | 69.1 | 32.5 | 219.6 | 220.3 | 219.6 | YES
7 | OK | 24 | 9 | 9 | 8 | 93 | 3.27 | 50 | 83.9 | 27.9 | 71.2 | 31.8 | 218.4 | 221.3 | 218.4 | YES
8 | OK | 4 | 5 | 22 | 2 | 8.4 | 6.65 | 50 | 83.9 | 27.9 | 58.1 | 32.4 | 221.9 | 223.2 | 221.9 | YES
9 | OK | 26 | 27 | 28 | 17 | 44.5 | 3.13 | 50 | 83.9 | 27.9 | 71.8 | 31.7 | 219.6 | 221.7 | 219.6 | YES
10 | OK | 9 | 8 | 8 | 8 | 131.9 | 2.98 | 50 | 83.9 | 27.9 | 72.3 | 31.5 | 218.4 | 221.8 | 218.4 | YES
11 | OK | 5 | 14 | 22 | 2 | 8.4 | 6.14 | 50 | 83.9 | 27.9 | 60 | 31.8 | 221.9 | 224.3 | 221.9 | YES
12 | OK | 27 | 30 | 28 | 17 | 44.5 | 2.51 | 50 | 83.9 | 27.9 | 74.2 | 30.9 | 219.7 | 222.9 | 219.7 | YES
13 | OK | 14 | 16 | 22 | 2 | 8.4 | 3.76 | 50 | 83.9 | 27.9 | 69.2 | 31.8 | 220.1 | 224.3 | 220.1 | YES
14 | OK | 30 | 32 | 28 | 17 | 44.5 | 2.04 | 50 | 83.9 | 27.9 | 76 | 30.4 | 219.7 | 223.7 | 219.7 | YES
15 | OK | 16 | 15 | 22 | 2 | 8.4 | 3.44 | 50 | 83.9 | 27.9 | 70.4 | 31.4 | 220.1 | 224.8 | 220.1 | YES
16 | OK | 32 | 31 | 28 | 17 | 44.5 | 1.86 | 50 | 83.9 | 27.9 | 76.7 | 30.1 | 219.7 | 224 | 219.7 | YES
17 | OK | 15 | 7 | 22 | 2 | 8.4 | 2.98 | 50 | 83.9 | 27.9 | 72.2 | 31.4 | 219.7 | 224.8 | 219.7 | YES
18 | OK | 7 | 6 | 22 | 2 | 8.4 | 2.98 | 50 | 83.9 | 27.9 | 72.2 | 31.4 | 219.7 | 224.8 | 219.7 | YES
19 | OK | 6 | 19 | 22 | 2 | 8.4 | 2.45 | 50 | 83.9 | 27.9 | 73.5 | 30.8 | 219.7 | 225.6 | 219.7 | YES
20 | OK | 19 | 20 | 22 | 2 | 8.4 | 2.45 | 50 | 83.9 | 27.9 | 74.3 | 30.8 | 219.7 | 225.6 | 219.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-030286
TR_B (available) | 27-008231
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 83.9
TR_B Baseline Loading% | 27.9
Total Scenarios Evaluated | 22
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 4
Tie Node (TR_A side) | 4
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 3.7
Load Transferred (kW) | 8.8
TR_A Loading After (%) | 49.8
TR_B Loading After (%) | 38.2
Minimum Voltage (V) | 222.8