## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 29 | 25 | 2 | 165.8 | 0.71 | 50 | 79.9 | 6 | 77.1 | 6 | 208.4 | 229.2 | 208.4 | NO
| NG | 16 | 22 | 12 | 3 | 122.1 | 14.1 | 50 | 79.9 | 6 | 23.4 | 38 | 221.7 | 201.1 | 201.1 | NO
| NG | 22 | 21 | 12 | 3 | 122.1 | 14.1 | 50 | 79.9 | 6 | 23.4 | 38 | 221.7 | 201.1 | 201.1 | NO
| NG | 21 | 20 | 12 | 3 | 122.1 | 13.44 | 50 | 79.9 | 6 | 25.9 | 38 | 221.2 | 201.1 | 201.1 | NO
| NG | 20 | 0 | 12 | 3 | 122.1 | 12.73 | 50 | 79.9 | 6 | 28.6 | 38 | 220.6 | 201.1 | 201.1 | NO
| NG | 0 | 1 | 12 | 3 | 122.1 | 11.3 | 50 | 79.9 | 6 | 34.1 | 34 | 220.6 | 206.7 | 206.7 | NO
1 | OK | 0 | 45 | 4 | 2 | 163.2 | 1.43 | 50 | 79.9 | 6 | 74 | 9.3 | 210.6 | 227.4 | 210.6 | YES
| NG | 1 | 14 | 12 | 3 | 122.1 | 10.19 | 50 | 79.9 | 6 | 38.4 | 31.1 | 220.6 | 209.3 | 209.3 | NO
2 | OK | 45 | 7 | 4 | 2 | 163.2 | 1.43 | 50 | 79.9 | 6 | 74 | 9.3 | 210.6 | 227.4 | 210.6 | YES
3 | OK | 14 | 13 | 12 | 3 | 122.1 | 9.7 | 50 | 79.9 | 6 | 40.3 | 29.8 | 220.6 | 210.4 | 210.4 | YES
4 | OK | 7 | 6 | 4 | 2 | 163.2 | 1.33 | 50 | 79.9 | 6 | 74.4 | 9.1 | 210.5 | 227.5 | 210.5 | YES
5 | ** OPTIMAL ** | 13 | 54 | 12 | 3 | 122.1 | 1.51 | 50 | 79.9 | 6 | 73.4 | 9.5 | 211.4 | 227.7 | 211.4 | YES
6 | OK | 6 | 36 | 36 | 2 | 228 | 1.33 | 50 | 79.9 | 6 | 74.4 | 9.1 | 210.5 | 227.7 | 210.5 | YES
7 | OK | 36 | 50 | 50 | 2 | 234.2 | 1.25 | 50 | 79.9 | 6 | 74.7 | 8.9 | 210.3 | 227.9 | 210.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-035255
TR_B (available) | 64-011528
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 79.9
TR_B Baseline Loading% | 6
Total Scenarios Evaluated | 14
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 54
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 3
Tie Line Distance (m) | 122.1
Load Transferred (kW) | 1.51
TR_A Loading After (%) | 73.4
TR_B Loading After (%) | 9.5
Minimum Voltage (V) | 211.4