## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 5 | 21 | 23 | 6.7 | 30.7 | 50 | 80.1 | 17.7 | 6.3 | 41.7 | 226 | 201.1 | 201.1 | NO
| NG | 5 | 7 | 21 | 23 | 6.7 | 29.05 | 50 | 80.1 | 17.7 | 10.1 | 40.4 | 226 | 200.3 | 200.3 | NO
| NG | 7 | 23 | 21 | 23 | 6.7 | 27.31 | 50 | 80.1 | 17.7 | 14 | 38.4 | 225.5 | 201.1 | 201.1 | NO
| NG | 23 | 22 | 21 | 23 | 6.7 | 26.67 | 50 | 80.1 | 17.7 | 15.5 | 38.4 | 225.5 | 201.1 | 201.1 | NO
| NG | 22 | 11 | 21 | 23 | 6.7 | 26.23 | 50 | 80.1 | 17.7 | 16.5 | 38.2 | 225.5 | 201 | 201 | NO
| NG | 11 | 12 | 21 | 23 | 6.7 | 24.93 | 50 | 80.1 | 17.7 | 16.6 | 37.2 | 225.5 | 200.7 | 200.7 | NO
| NG | 12 | 34 | 21 | 23 | 6.7 | 22.58 | 50 | 80.1 | 17.7 | 25 | 35.4 | 223.8 | 200.3 | 200.3 | NO
| NG | 34 | 28 | 21 | 23 | 6.7 | 22.58 | 50 | 80.1 | 17.7 | 25 | 35.4 | 223.8 | 200.3 | 200.3 | NO
| NG | 28 | 19 | 21 | 23 | 6.7 | 20.71 | 50 | 80.1 | 17.7 | 29.3 | 34.1 | 222.8 | 200 | 200 | NO
| NG | 19 | 20 | 21 | 23 | 6.7 | 19.28 | 50 | 80.1 | 17.7 | 32.6 | 33.1 | 222.6 | 199.4 | 199.4 | NO
| NG | 20 | 35 | 21 | 23 | 6.7 | 18.91 | 50 | 80.1 | 17.7 | 33.5 | 32.8 | 222 | 199.4 | 199.4 | NO
| NG | 35 | 29 | 21 | 23 | 6.7 | 18.91 | 50 | 80.1 | 17.7 | 33.5 | 32.8 | 222 | 199.4 | 199.4 | NO
| NG | 29 | 15 | 21 | 23 | 6.7 | 6.51 | 50 | 80.1 | 17.7 | 63.8 | 22.5 | 209.1 | 221.5 | 209.1 | NO
1 | ** OPTIMAL ** | 15 | 16 | 21 | 23 | 6.7 | 3.08 | 50 | 80.1 | 17.7 | 71.7 | 20 | 210.2 | 221.5 | 210.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-035357
TR_B (available) | 49-003833
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.1
TR_B Baseline Loading% | 17.7
Total Scenarios Evaluated | 14
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 16
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 23
Tie Line Distance (m) | 6.7
Load Transferred (kW) | 3.08
TR_A Loading After (%) | 71.7
TR_B Loading After (%) | 20
Minimum Voltage (V) | 210.2