## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 5 | 15 | 15 | 46.9 | 30.7 | 50 | 80.1 | 24.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 5 | 7 | 15 | 15 | 46.9 | 29.05 | 50 | 80.1 | 24.5 | 10.1 | 47.8 | 226 | 192.4 | 192.4 | NO
| NG | 7 | 23 | 15 | 15 | 46.9 | 27.31 | 50 | 80.1 | 24.5 | 14 | 45.8 | 225.5 | 193.5 | 193.5 | NO
| NG | 23 | 22 | 15 | 15 | 46.9 | 26.67 | 50 | 80.1 | 24.5 | 15.5 | 45.8 | 225.5 | 193.5 | 193.5 | NO
| NG | 22 | 11 | 15 | 15 | 46.9 | 26.23 | 50 | 80.1 | 24.5 | 16.5 | 45.5 | 225.5 | 193.3 | 193.3 | NO
| NG | 11 | 12 | 15 | 15 | 46.9 | 24.93 | 50 | 80.1 | 24.5 | 16.6 | 44.5 | 225.5 | 192.9 | 192.9 | NO
| NG | 12 | 10 | 9 | 68 | 196.9 | 2.35 | 50 | 80.1 | 24.5 | 74.5 | 26.3 | 202 | 218.6 | 202 | NO
| NG | 12 | 34 | 15 | 15 | 46.9 | 22.58 | 50 | 80.1 | 24.5 | 25 | 42.6 | 223.8 | 192.4 | 192.4 | NO
| NG | 10 | 8 | 9 | 68 | 196.9 | 0.89 | 50 | 80.1 | 24.5 | 75.4 | 25.1 | 202 | 222.7 | 202 | NO
| NG | 34 | 28 | 15 | 15 | 46.9 | 22.58 | 50 | 80.1 | 24.5 | 25 | 42.6 | 223.8 | 192.4 | 192.4 | NO
| NG | 8 | 9 | 9 | 68 | 196.9 | 0.62 | 50 | 80.1 | 24.5 | 78.6 | 23.6 | 202.1 | 7 | 7 | NO
| NG | 28 | 24 | 25 | 68 | 140.5 | 1.87 | 50 | 80.1 | 24.5 | 75.8 | 25.9 | 201.9 | 220.2 | 201.9 | NO
| NG | 28 | 19 | 15 | 15 | 46.9 | 20.71 | 50 | 80.1 | 24.5 | 29.3 | 41.3 | 222.8 | 192 | 192 | NO
| NG | 24 | 25 | 25 | 68 | 140.5 | 1.21 | 50 | 80.1 | 24.5 | 77.3 | 24.5 | 202 | 224.9 | 202 | NO
| NG | 19 | 20 | 15 | 15 | 46.9 | 19.28 | 50 | 80.1 | 24.5 | 32.6 | 40.3 | 222.6 | 191.2 | 191.2 | NO
| NG | 19 | 17 | 17 | 68 | 122.1 | 1.25 | 50 | 80.1 | 24.5 | 77.2 | 25.4 | 201.7 | 225 | 201.7 | NO
| NG | 20 | 35 | 15 | 15 | 46.9 | 18.91 | 50 | 80.1 | 24.5 | 33.5 | 40 | 222 | 191.1 | 191.1 | NO
| NG | 17 | 18 | 18 | 68 | 128.8 | 1.08 | 50 | 80.1 | 24.5 | 77.6 | 25.3 | 201.8 | 225 | 201.8 | NO
| NG | 35 | 29 | 15 | 15 | 46.9 | 18.91 | 50 | 80.1 | 24.5 | 33.5 | 40 | 222 | 191.1 | 191.1 | NO
| NG | 29 | 15 | 15 | 15 | 46.9 | 6.51 | 50 | 80.1 | 24.5 | 63.8 | 29.3 | 209.1 | 222 | 209.1 | NO
1 | ** OPTIMAL ** | 15 | 16 | 16 | 16 | 49.4 | 3.08 | 50 | 80.1 | 24.5 | 71.7 | 26.7 | 210.2 | 222.5 | 210.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-035357
TR_B (available) | 67-038648
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.1
TR_B Baseline Loading% | 24.5
Total Scenarios Evaluated | 21
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 16
Tie Node (TR_A side) | 16
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 49.4
Load Transferred (kW) | 3.08
TR_A Loading After (%) | 71.7
TR_B Loading After (%) | 26.7
Minimum Voltage (V) | 210.2