## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 37 | 34 | 34 | 13 | 46.9 | 14.06 | 50 | 82.8 | 41.8 | 19.2 | 75.6 | 225.3 | 204.7 | 204.7 | NO
1 | OK | 37 | 38 | 45 | 46 | 45.8 | 8.33 | 50 | 82.8 | 41.8 | 63.5 | 61.2 | 212.7 | 218.7 | 212.7 | YES
2 | OK | 37 | 54 | 55 | 2 | 48.2 | 12.81 | 50 | 82.8 | 41.8 | 52.1 | 41.8 | 213.5 | 219.4 | 213.5 | YES
| NG | 34 | 33 | 28 | 4 | 47.7 | 13.64 | 50 | 82.8 | 41.8 | 20.2 | 75 | 225.1 | 203.9 | 203.9 | NO
3 | OK | 38 | 39 | 45 | 46 | 45.8 | 7.97 | 50 | 82.8 | 41.8 | 64.3 | 60.4 | 212.7 | 218.7 | 212.7 | YES
4 | OK | 54 | 55 | 55 | 2 | 48.2 | 11.65 | 50 | 82.8 | 41.8 | 52.5 | 41.8 | 213.5 | 219.4 | 213.5 | YES
| NG | 33 | 32 | 28 | 4 | 47.7 | 13.48 | 50 | 82.8 | 41.8 | 20.6 | 74.6 | 225.1 | 203.9 | 203.9 | NO
5 | OK | 39 | 40 | 45 | 46 | 45.8 | 7.97 | 50 | 82.8 | 41.8 | 64.3 | 59.5 | 212.7 | 218.8 | 212.7 | YES
| NG | 55 | 56 | 1 | 39 | 100.5 | 9.66 | 50 | 82.8 | 41.8 | 57.1 | 59.5 | 213.7 | 198.1 | 198.1 | NO
6 | OK | 55 | 57 | 57 | 3 | 49.7 | 1.99 | 50 | 82.8 | 41.8 | 78 | 41.8 | 211.7 | 219.4 | 211.7 | YES
| NG | 32 | 29 | 28 | 4 | 47.7 | 12.74 | 50 | 82.8 | 41.8 | 20.6 | 72.9 | 225.1 | 203.8 | 203.8 | NO
7 | OK | 40 | 41 | 45 | 46 | 45.8 | 7.59 | 50 | 82.8 | 41.8 | 65.2 | 59.5 | 212.6 | 218.8 | 212.6 | YES
| NG | 56 | 0 | 1 | 39 | 100.5 | 8.44 | 50 | 82.8 | 41.8 | 60.1 | 59.5 | 213.9 | 198.1 | 198.1 | NO
| NG | 29 | 27 | 28 | 4 | 47.7 | 12.34 | 50 | 82.8 | 41.8 | 23.2 | 71.8 | 224.9 | 204.8 | 204.8 | NO
8 | OK | 41 | 42 | 45 | 46 | 45.8 | 6.96 | 50 | 82.8 | 41.8 | 66.6 | 58 | 212.6 | 218.8 | 212.6 | YES
| NG | 0 | 49 | 49 | 24 | 124.6 | 7.32 | 50 | 82.8 | 41.8 | 60.1 | 56.7 | 213.9 | 197.4 | 197.4 | NO
9 | ** OPTIMAL ** | 27 | 26 | 26 | 6 | 74.3 | 5.14 | 50 | 82.8 | 41.8 | 48 | 53.9 | 217.4 | 219.4 | 217.4 | YES
10 | OK | 27 | 31 | 28 | 4 | 47.7 | 7.2 | 50 | 82.8 | 41.8 | 57.6 | 59.2 | 213.2 | 211.9 | 211.9 | YES
11 | OK | 42 | 44 | 45 | 46 | 45.8 | 6.03 | 50 | 82.8 | 41.8 | 68.8 | 55.8 | 212.6 | 218.8 | 212.6 | YES
12 | OK | 26 | 25 | 25 | 6 | 106.8 | 4.03 | 50 | 82.8 | 41.8 | 50.6 | 51.2 | 216.2 | 219.6 | 216.2 | YES
13 | OK | 31 | 30 | 28 | 4 | 47.7 | 7.2 | 50 | 82.8 | 41.8 | 58 | 59.2 | 213 | 211.9 | 211.9 | YES
14 | OK | 44 | 45 | 45 | 46 | 45.8 | 6.03 | 50 | 82.8 | 41.8 | 68.8 | 52 | 212.6 | 218.8 | 212.6 | YES
15 | OK | 25 | 24 | 24 | 7 | 135.9 | 3.3 | 50 | 82.8 | 41.8 | 52.3 | 49.5 | 215.6 | 219.9 | 215.6 | YES
16 | OK | 30 | 28 | 28 | 4 | 47.7 | 6.86 | 50 | 82.8 | 41.8 | 58.8 | 58.3 | 212.6 | 211.7 | 211.7 | YES
17 | OK | 45 | 43 | 62 | 45 | 46.8 | 2.8 | 50 | 82.8 | 41.8 | 76.3 | 45.4 | 212.6 | 219.4 | 212.6 | YES
18 | OK | 45 | 65 | 67 | 20 | 149.5 | 1.59 | 50 | 82.8 | 41.8 | 79.1 | 45.5 | 212 | 219.4 | 212 | YES
19 | OK | 24 | 73 | 73 | 7 | 141.8 | 2.83 | 50 | 82.8 | 41.8 | 53.4 | 47.3 | 215.1 | 219.9 | 215.1 | YES
20 | OK | 28 | 22 | 22 | 2 | 49.4 | 6.53 | 50 | 82.8 | 41.8 | 59.6 | 57.6 | 212.7 | 211.9 | 211.9 | YES
21 | OK | 43 | 62 | 62 | 45 | 46.8 | 1.53 | 50 | 82.8 | 41.8 | 79.2 | 45.4 | 212 | 219.4 | 212 | YES
22 | OK | 65 | 66 | 67 | 20 | 149.5 | 1.59 | 50 | 82.8 | 41.8 | 79.1 | 45.5 | 212 | 219.4 | 212 | YES
23 | OK | 22 | 21 | 21 | 2 | 51.6 | 6.53 | 50 | 82.8 | 41.8 | 64.2 | 57.6 | 213 | 211.9 | 211.9 | YES
24 | OK | 66 | 67 | 67 | 20 | 149.5 | 1.59 | 50 | 82.8 | 41.8 | 79.1 | 42.2 | 212 | 219.4 | 212 | YES
25 | OK | 21 | 20 | 20 | 3 | 80.1 | 6.2 | 50 | 82.8 | 41.8 | 65 | 56.8 | 213 | 211.8 | 211.8 | YES
26 | OK | 20 | 19 | 19 | 3 | 115.2 | 5.7 | 50 | 82.8 | 41.8 | 66.2 | 55.7 | 213.1 | 211.8 | 211.8 | YES
27 | OK | 19 | 18 | 18 | 39 | 149.3 | 4.86 | 50 | 82.8 | 41.8 | 68.2 | 53.7 | 213.1 | 212.7 | 212.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-035384
TR_B (available) | 60-004774
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 82.8
TR_B Baseline Loading% | 41.8
Total Scenarios Evaluated | 35
Feasible Scenarios | 27
--- Optimal Solution ---
Switch Parent Node | 27
Switch Child Node | 26
Tie Node (TR_A side) | 26
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 74.3
Load Transferred (kW) | 5.14
TR_A Loading After (%) | 48
TR_B Loading After (%) | 53.9
Minimum Voltage (V) | 217.4