## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 7 | 43 | 67 | 2 | 17.95 | 50 | 93 | 24.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 50 | 8 | 25 | 72 | 2.3 | 20.66 | 50 | 93 | 24.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 7 | 6 | 43 | 67 | 2 | 17.82 | 50 | 93 | 24.7 | 51.1 | 34.1 | 214.9 | 219.6 | 214.9 | YES
2 | OK | 8 | 9 | 25 | 72 | 2.3 | 20.66 | 50 | 93 | 24.7 | 44.4 | 32.6 | 215.7 | 212.2 | 212.2 | YES
3 | OK | 6 | 5 | 43 | 67 | 2 | 16.99 | 50 | 93 | 24.7 | 53 | 33.1 | 214.9 | 221.3 | 214.9 | YES
4 | OK | 9 | 10 | 25 | 72 | 2.3 | 20.66 | 50 | 93 | 24.7 | 44.4 | 32.6 | 215.9 | 212.2 | 212.2 | YES
5 | OK | 5 | 55 | 43 | 67 | 2 | 14.93 | 50 | 93 | 24.7 | 57.8 | 31.9 | 214.8 | 222.9 | 214.8 | YES
6 | OK | 10 | 11 | 25 | 72 | 2.3 | 20.4 | 50 | 93 | 24.7 | 45 | 32.3 | 215.8 | 213.2 | 213.2 | YES
7 | OK | 55 | 0 | 43 | 67 | 2 | 14.93 | 50 | 93 | 24.7 | 57.8 | 31.9 | 214.8 | 222.9 | 214.8 | YES
8 | OK | 11 | 12 | 25 | 72 | 2.3 | 20.22 | 50 | 93 | 24.7 | 45.4 | 32 | 215.7 | 213.8 | 213.8 | YES
9 | OK | 0 | 1 | 43 | 67 | 2 | 14.47 | 50 | 93 | 24.7 | 58.8 | 31.8 | 214.8 | 223 | 214.8 | YES
10 | ** OPTIMAL ** | 12 | 13 | 25 | 72 | 2.3 | 19.8 | 50 | 93 | 24.7 | 46.3 | 31.5 | 215.5 | 215.2 | 215.2 | YES
11 | OK | 1 | 38 | 43 | 67 | 2 | 12.16 | 50 | 93 | 24.7 | 64.1 | 31.4 | 213.8 | 223.3 | 213.8 | YES
12 | OK | 13 | 14 | 25 | 72 | 2.3 | 16.6 | 50 | 93 | 24.7 | 53.7 | 29.4 | 214.7 | 220.3 | 214.7 | YES
13 | OK | 38 | 39 | 43 | 67 | 2 | 12.16 | 50 | 93 | 24.7 | 64.1 | 31.4 | 213.8 | 223.3 | 213.8 | YES
14 | OK | 14 | 15 | 25 | 72 | 2.3 | 16.3 | 50 | 93 | 24.7 | 54.4 | 29 | 214.5 | 221.1 | 214.5 | YES
15 | OK | 39 | 40 | 43 | 67 | 2 | 12.16 | 50 | 93 | 24.7 | 64.1 | 31.4 | 213.8 | 223.3 | 213.8 | YES
16 | OK | 15 | 16 | 25 | 72 | 2.3 | 16.01 | 50 | 93 | 24.7 | 55.1 | 28.7 | 214.4 | 221.8 | 214.4 | YES
17 | OK | 40 | 54 | 43 | 67 | 2 | 12.12 | 50 | 93 | 24.7 | 64.2 | 31.4 | 213.8 | 223.3 | 213.8 | YES
18 | OK | 16 | 56 | 25 | 72 | 2.3 | 16.01 | 50 | 93 | 24.7 | 55.1 | 28.7 | 214.4 | 221.8 | 214.4 | YES
| NG | 54 | 31 | 43 | 67 | 2 | 12.1 | 50 | 93 | 24.7 | 17.7 | 31.4 | 5.4 | 223.3 | 5.4 | NO
19 | OK | 56 | 17 | 25 | 72 | 2.3 | 15.87 | 50 | 93 | 24.7 | 55.4 | 28.5 | 214.3 | 222.1 | 214.3 | YES
20 | OK | 17 | 18 | 25 | 72 | 2.3 | 10.87 | 50 | 93 | 24.7 | 67.1 | 28.3 | 214.2 | 222.4 | 214.2 | YES
21 | OK | 18 | 20 | 25 | 72 | 2.3 | 8.45 | 50 | 93 | 24.7 | 72.8 | 27.1 | 213.7 | 225.3 | 213.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-035410
TR_B (available) | 34-010151
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 93
TR_B Baseline Loading% | 24.7
Total Scenarios Evaluated | 24
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 13
Tie Node (TR_A side) | 25
Tie Node (TR_B side) | 72
Tie Line Distance (m) | 2.3
Load Transferred (kW) | 19.8
TR_A Loading After (%) | 46.3
TR_B Loading After (%) | 31.5
Minimum Voltage (V) | 215.2