## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 4 | 3 | 18 | 10 | 2.2 | 6.99 | 50 | 89.5 | 33.6 | 62.5 | 61.3 | 215.2 | 211.3 | 211.3 | YES
| NG | 4 | 22 | 33 | 12 | 2.7 | 13.9 | 50 | 89.5 | 33.6 | 35.2 | 88.3 | 224.9 | 213.1 | 213.1 | NO
2 | OK | 3 | 5 | 18 | 10 | 2.2 | 5.28 | 50 | 89.5 | 33.6 | 69.1 | 54.4 | 214.7 | 214 | 214 | YES
| NG | 22 | 21 | 21 | 12 | 85.4 | 13.9 | 50 | 89.5 | 33.6 | 35.2 | 88.3 | 224.9 | 213.1 | 213.1 | NO
3 | OK | 5 | 15 | 18 | 10 | 2.2 | 5.28 | 50 | 89.5 | 33.6 | 69.1 | 52.1 | 214.7 | 215.4 | 214.7 | YES
4 | OK | 21 | 23 | 23 | 12 | 120.4 | 11.62 | 50 | 89.5 | 33.6 | 43.9 | 79.5 | 223 | 212.8 | 212.8 | YES
5 | OK | 15 | 14 | 18 | 10 | 2.2 | 4.72 | 50 | 89.5 | 33.6 | 71.2 | 52.1 | 214.7 | 215.4 | 214.7 | YES
6 | OK | 23 | 27 | 25 | 12 | 137.6 | 11.33 | 50 | 89.5 | 33.6 | 45.1 | 67.8 | 222.8 | 213.2 | 213.2 | YES
7 | OK | 14 | 7 | 18 | 10 | 2.2 | 2.87 | 50 | 89.5 | 33.6 | 78.4 | 44.7 | 214.7 | 220.6 | 214.7 | YES
8 | OK | 27 | 20 | 25 | 12 | 137.6 | 11.17 | 50 | 89.5 | 33.6 | 45.1 | 67.8 | 222.8 | 213.2 | 213.2 | YES
9 | OK | 7 | 6 | 18 | 10 | 2.2 | 2.87 | 50 | 89.5 | 33.6 | 78.4 | 44.7 | 214.7 | 220.6 | 214.7 | YES
10 | OK | 20 | 19 | 25 | 12 | 137.6 | 10.15 | 50 | 89.5 | 33.6 | 49.6 | 67.8 | 221.8 | 213.2 | 213.2 | YES
11 | OK | 19 | 29 | 25 | 12 | 137.6 | 8.61 | 50 | 89.5 | 33.6 | 55.6 | 67.8 | 220.3 | 213.2 | 213.2 | YES
12 | ** OPTIMAL ** | 29 | 30 | 25 | 12 | 137.6 | 3.91 | 50 | 89.5 | 33.6 | 73.8 | 48.7 | 220.5 | 222.9 | 220.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 63-036041
TR_B (available) | 59-013955
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 89.5
TR_B Baseline Loading% | 33.6
Total Scenarios Evaluated | 14
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 30
Tie Node (TR_A side) | 25
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 137.6
Load Transferred (kW) | 3.91
TR_A Loading After (%) | 73.8
TR_B Loading After (%) | 48.7
Minimum Voltage (V) | 220.5