## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 78 | 27 | 27 | 2 | 102.4 | 10.23 | 50 | 67.2 | 58 | 55.2 | 82.5 | 217.3 | 213.9 | 213.9 | NO
1 | OK | 78 | 112 | 20 | 2 | 8.7 | 5.05 | 50 | 67.2 | 58 | 61.3 | 69.8 | 216.8 | 219.4 | 216.8 | YES
| NG | 27 | 28 | 28 | 2 | 114.4 | 10.21 | 50 | 67.2 | 58 | 55.3 | 82.4 | 217.3 | 214.3 | 214.3 | NO
2 | OK | 112 | 111 | 20 | 2 | 8.7 | 5.05 | 50 | 67.2 | 58 | 61.3 | 69.8 | 216.8 | 219.4 | 216.8 | YES
| NG | 28 | 29 | 29 | 2 | 115.4 | 10.03 | 50 | 67.2 | 58 | 55.5 | 82 | 217.3 | 214.3 | 214.3 | NO
3 | OK | 111 | 126 | 20 | 2 | 8.7 | 5 | 50 | 67.2 | 58 | 61.4 | 69.7 | 216.8 | 219.4 | 216.8 | YES
| NG | 29 | 30 | 30 | 2 | 136.6 | 9.6 | 50 | 67.2 | 58 | 56 | 80.9 | 217.2 | 214.6 | 214.6 | NO
4 | OK | 126 | 118 | 20 | 2 | 8.7 | 5 | 50 | 67.2 | 58 | 61.4 | 69.7 | 216.8 | 219.4 | 216.8 | YES
5 | OK | 118 | 102 | 20 | 2 | 8.7 | 4.86 | 50 | 67.2 | 58 | 61.6 | 69.4 | 216.8 | 219.5 | 216.8 | YES
6 | OK | 102 | 20 | 20 | 2 | 8.7 | 3 | 50 | 67.2 | 58 | 63.7 | 65 | 216.8 | 219.5 | 216.8 | YES
7 | ** OPTIMAL ** | 20 | 21 | 21 | 2 | 53.3 | 3 | 50 | 67.2 | 58 | 63.7 | 65 | 216.8 | 219.5 | 216.8 | YES
8 | OK | 21 | 22 | 23 | 28 | 91.9 | 2.54 | 50 | 67.2 | 58 | 64.2 | 64 | 216.7 | 219.5 | 216.7 | YES
9 | OK | 22 | 23 | 23 | 28 | 91.9 | 1.91 | 50 | 67.2 | 58 | 65 | 62.5 | 216.7 | 219.6 | 216.7 | YES
10 | OK | 23 | 24 | 24 | 29 | 92.4 | 1.54 | 50 | 67.2 | 58 | 65.4 | 61.6 | 216.6 | 219.6 | 216.6 | YES
11 | OK | 24 | 25 | 25 | 30 | 96.3 | 0.81 | 50 | 67.2 | 58 | 66.3 | 59.9 | 216.6 | 220 | 216.6 | YES
12 | OK | 25 | 26 | 26 | 30 | 96.9 | 0.12 | 50 | 67.2 | 58 | 67.1 | 58.3 | 216.6 | 220.2 | 216.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-002071
TR_B (available) | 63-035409
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 67.2
TR_B Baseline Loading% | 58
Total Scenarios Evaluated | 16
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 20
Switch Child Node | 21
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 53.3
Load Transferred (kW) | 3
TR_A Loading After (%) | 63.7
TR_B Loading After (%) | 65
Minimum Voltage (V) | 216.8