## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 74 | 75 | 69 | 6 | 0.6 | 13.42 | 50 | 67.2 | 12.4 | 51.5 | 24.5 | 217.3 | 218.8 | 217.3 | YES
2 | OK | 75 | 76 | 69 | 6 | 0.6 | 13.39 | 50 | 67.2 | 12.4 | 51.5 | 24.5 | 217.3 | 218.8 | 217.3 | YES
3 | ** OPTIMAL ** | 76 | 72 | 69 | 6 | 0.6 | 12.83 | 50 | 67.2 | 12.4 | 52.2 | 24.5 | 217.3 | 218.8 | 217.3 | YES
4 | OK | 72 | 70 | 69 | 6 | 0.6 | 12.45 | 50 | 67.2 | 12.4 | 52.6 | 23 | 217.2 | 220.3 | 217.2 | YES
5 | OK | 70 | 71 | 69 | 6 | 0.6 | 10.5 | 50 | 67.2 | 12.4 | 54.9 | 21.3 | 217.1 | 222 | 217.1 | YES
6 | OK | 71 | 104 | 69 | 6 | 0.6 | 9.71 | 50 | 67.2 | 12.4 | 55.8 | 21.3 | 217.1 | 222 | 217.1 | YES
7 | OK | 104 | 61 | 69 | 6 | 0.6 | 9.61 | 50 | 67.2 | 12.4 | 55.9 | 21.3 | 217.1 | 222 | 217.1 | YES
8 | OK | 61 | 62 | 69 | 6 | 0.6 | 8.64 | 50 | 67.2 | 12.4 | 57 | 20 | 217 | 222.9 | 217 | YES
9 | OK | 62 | 73 | 69 | 6 | 0.6 | 8.49 | 50 | 67.2 | 12.4 | 57.2 | 20 | 217 | 222.9 | 217 | YES
10 | OK | 73 | 106 | 69 | 6 | 0.6 | 4.08 | 50 | 67.2 | 12.4 | 62.4 | 19.2 | 217 | 223.8 | 217 | YES
11 | OK | 106 | 63 | 69 | 6 | 0.6 | 3.97 | 50 | 67.2 | 12.4 | 62.5 | 19.2 | 217 | 223.8 | 217 | YES
12 | OK | 63 | 64 | 69 | 6 | 0.6 | 3.47 | 50 | 67.2 | 12.4 | 63.1 | 18.8 | 217 | 224 | 217 | YES
13 | OK | 64 | 65 | 69 | 6 | 0.6 | 3.06 | 50 | 67.2 | 12.4 | 63.6 | 18.6 | 216.9 | 224.2 | 216.9 | YES
14 | OK | 65 | 66 | 69 | 6 | 0.6 | 1.95 | 50 | 67.2 | 12.4 | 64.9 | 17.6 | 216.4 | 224.7 | 216.4 | YES
15 | OK | 66 | 67 | 69 | 6 | 0.6 | 0.49 | 50 | 67.2 | 12.4 | 66.6 | 14 | 216.7 | 226.7 | 216.7 | YES
16 | OK | 67 | 108 | 69 | 6 | 0.6 | 0.41 | 50 | 67.2 | 12.4 | 66.7 | 14 | 216.7 | 226.7 | 216.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-002071
TR_B (available) | 68-003146
TR_A Rated kVA | 100
TR_B Rated kVA | 30
TR_A Baseline Loading% | 67.2
TR_B Baseline Loading% | 12.4
Total Scenarios Evaluated | 16
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 76
Switch Child Node | 72
Tie Node (TR_A side) | 69
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 0.6
Load Transferred (kW) | 12.83
TR_A Loading After (%) | 52.2
TR_B Loading After (%) | 24.5
Minimum Voltage (V) | 217.3