## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 26 | 68 | 18 | 76.9 | 49.02 | 50 | 86.6 | 29.5 | 28 | 48.4 | 221.4 | 188.8 | 188.8 | NO
| NG | 26 | 36 | 68 | 18 | 76.9 | 46.91 | 50 | 86.6 | 29.5 | 28 | 47.6 | 221.4 | 190.2 | 190.2 | NO
| NG | 36 | 37 | 68 | 18 | 76.9 | 46.91 | 50 | 86.6 | 29.5 | 30.4 | 47.6 | 221.2 | 190.2 | 190.2 | NO
| NG | 37 | 44 | 68 | 18 | 76.9 | 38.94 | 50 | 86.6 | 29.5 | 39.6 | 43.6 | 220.6 | 197.6 | 197.6 | NO
| NG | 44 | 78 | 68 | 18 | 76.9 | 35.76 | 50 | 86.6 | 29.5 | 43.3 | 40.4 | 220.4 | 203.5 | 203.5 | NO
| NG | 78 | 0 | 68 | 18 | 76.9 | 34.34 | 50 | 86.6 | 29.5 | 44.9 | 40.4 | 220.1 | 203.5 | 203.5 | NO
| NG | 0 | 1 | 68 | 18 | 76.9 | 34.34 | 50 | 86.6 | 29.5 | 44.9 | 40.4 | 220.1 | 203.5 | 203.5 | NO
| NG | 1 | 72 | 68 | 18 | 76.9 | 33.66 | 50 | 86.6 | 29.5 | 45.7 | 39.5 | 220.1 | 205.2 | 205.2 | NO
| NG | 72 | 30 | 20 | 18 | 121.3 | 29.25 | 50 | 86.6 | 29.5 | 49.6 | 37.8 | 219.8 | 209.5 | 209.5 | NO
| NG | 30 | 27 | 20 | 18 | 121.3 | 29.25 | 50 | 86.6 | 29.5 | 49.6 | 37.8 | 219.8 | 209.5 | 209.5 | NO
| NG | 27 | 28 | 20 | 18 | 121.3 | 29.25 | 50 | 86.6 | 29.5 | 50.8 | 37.8 | 219.6 | 209.5 | 209.5 | NO
1 | OK | 28 | 33 | 20 | 18 | 121.3 | 23.35 | 50 | 86.6 | 29.5 | 57.6 | 34.9 | 219.2 | 216.5 | 216.5 | YES
2 | OK | 33 | 6 | 20 | 18 | 121.3 | 23.27 | 50 | 86.6 | 29.5 | 57.7 | 34.9 | 219.2 | 216.5 | 216.5 | YES
| NG | 6 | 7 | 20 | 18 | 121.3 | 23.27 | 50 | 86.6 | 29.5 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 29.5% (degenerate)
| NG | 7 | 8 | 20 | 18 | 121.3 | 22.92 | 50 | 86.6 | 29.5 | 58.1 | 50.7 | 219.2 | 6 | 6 | NO
3 | OK | 8 | 79 | 20 | 18 | 121.3 | 22.92 | 50 | 86.6 | 29.5 | 58.1 | 34.5 | 219.2 | 217.4 | 217.4 | YES
4 | OK | 79 | 10 | 20 | 18 | 121.3 | 22.92 | 50 | 86.6 | 29.5 | 58.1 | 34.5 | 219.2 | 217.4 | 217.4 | YES
5 | OK | 10 | 9 | 20 | 18 | 121.3 | 22.92 | 50 | 86.6 | 29.5 | 58.1 | 34.5 | 219.2 | 217.4 | 217.4 | YES
6 | OK | 9 | 16 | 20 | 18 | 121.3 | 22.53 | 50 | 86.6 | 29.5 | 58.6 | 34 | 219.2 | 218.3 | 218.3 | YES
7 | ** OPTIMAL ** | 16 | 15 | 20 | 18 | 121.3 | 16.72 | 50 | 86.6 | 29.5 | 65.4 | 32.4 | 218.6 | 220.1 | 218.6 | YES
8 | OK | 15 | 31 | 20 | 18 | 121.3 | 14.83 | 50 | 86.6 | 29.5 | 67.7 | 32.4 | 216.1 | 220.1 | 216.1 | YES
9 | OK | 31 | 17 | 20 | 18 | 121.3 | 14.42 | 50 | 86.6 | 29.5 | 68.2 | 32.4 | 215.4 | 220.1 | 215.4 | YES
| NG | 17 | 3 | 3 | 18 | 175.7 | 11.96 | 50 | 86.6 | 29.5 | 71.2 | 46.6 | 215.5 | 188.5 | 188.5 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 64-004667
TR_B (available) | 62-001681
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 86.6
TR_B Baseline Loading% | 29.5
Total Scenarios Evaluated | 23
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 15
Tie Node (TR_A side) | 20
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 121.3
Load Transferred (kW) | 16.72
TR_A Loading After (%) | 65.4
TR_B Loading After (%) | 32.4
Minimum Voltage (V) | 218.6