## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 34 | 45 | 37 | 49.2 | 21.38 | 50 | 86.6 | 25.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 35 | 25 | 23 | 29 | 70.5 | 51.8 | 50 | 86.6 | 25.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 34 | 50 | 45 | 37 | 49.2 | 19.39 | 50 | 86.6 | 25.3 | 64 | 43 | 202 | 176.7 | 176.7 | NO
| NG | 25 | 26 | 23 | 29 | 70.5 | 49.02 | 50 | 86.6 | 25.3 | 28 | 37 | 221.4 | 194.4 | 194.4 | NO
| NG | 50 | 51 | 45 | 37 | 49.2 | 19.12 | 50 | 86.6 | 25.3 | 64.3 | 40.8 | 201.9 | 182.7 | 182.7 | NO
| NG | 26 | 36 | 23 | 29 | 70.5 | 46.91 | 50 | 86.6 | 25.3 | 28 | 36.5 | 221.4 | 195.6 | 195.6 | NO
| NG | 51 | 48 | 45 | 37 | 49.2 | 7.04 | 50 | 86.6 | 25.3 | 78.4 | 30.8 | 201.6 | 213.4 | 201.6 | NO
| NG | 36 | 37 | 23 | 29 | 70.5 | 46.91 | 50 | 86.6 | 25.3 | 30.4 | 36.5 | 221.2 | 195.6 | 195.6 | NO
| NG | 48 | 46 | 45 | 37 | 49.2 | 6.77 | 50 | 86.6 | 25.3 | 78.7 | 30.5 | 201.5 | 213.9 | 201.5 | NO
| NG | 37 | 44 | 23 | 29 | 70.5 | 38.94 | 50 | 86.6 | 25.3 | 39.6 | 34.1 | 220.6 | 202.1 | 202.1 | NO
| NG | 37 | 38 | 40 | 17 | 70.5 | 7.97 | 50 | 86.6 | 25.3 | 77.2 | 31.2 | 202.7 | 222.8 | 202.7 | NO
| NG | 44 | 78 | 23 | 29 | 70.5 | 35.76 | 50 | 86.6 | 25.3 | 43.3 | 32.1 | 220.4 | 207.3 | 207.3 | NO
| NG | 38 | 39 | 40 | 17 | 70.5 | 7.35 | 50 | 86.6 | 25.3 | 77.9 | 30.7 | 202.7 | 222.9 | 202.7 | NO
| NG | 78 | 0 | 23 | 29 | 70.5 | 34.34 | 50 | 86.6 | 25.3 | 44.9 | 32.1 | 220.1 | 207.3 | 207.3 | NO
| NG | 0 | 1 | 23 | 29 | 70.5 | 34.34 | 50 | 86.6 | 25.3 | 44.9 | 32.1 | 220.1 | 207.3 | 207.3 | NO
| NG | 1 | 72 | 23 | 29 | 70.5 | 33.66 | 50 | 86.6 | 25.3 | 45.7 | 31.5 | 220.1 | 208.9 | 208.9 | NO
1 | OK | 72 | 30 | 23 | 29 | 70.5 | 29.25 | 50 | 86.6 | 25.3 | 49.6 | 30.5 | 219.8 | 211.5 | 211.5 | YES
2 | OK | 30 | 27 | 23 | 29 | 70.5 | 29.25 | 50 | 86.6 | 25.3 | 49.6 | 30.5 | 219.8 | 211.5 | 211.5 | YES
3 | OK | 27 | 28 | 23 | 29 | 70.5 | 29.25 | 50 | 86.6 | 25.3 | 50.8 | 30.5 | 219.6 | 211.5 | 211.5 | YES
4 | OK | 28 | 33 | 33 | 29 | 125.4 | 23.35 | 50 | 86.6 | 25.3 | 57.6 | 28.8 | 219.2 | 216.2 | 216.2 | YES
5 | ** OPTIMAL ** | 33 | 6 | 6 | 29 | 130.2 | 23.27 | 50 | 86.6 | 25.3 | 57.7 | 28.8 | 219.2 | 216.4 | 216.4 | YES
| NG | 6 | 7 | 7 | 29 | 132.4 | 23.27 | 50 | 86.6 | 25.3 | 57.7 | 25.5 | 219.2 | 7.8 | 7.8 | NO
| NG | 7 | 8 | 8 | 29 | 147.7 | 22.92 | 50 | 86.6 | 25.3 | 58.1 | 3801.8 | 219.2 | 99.9 | 99.9 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 64-004667
TR_B (available) | 65-034282
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 86.6
TR_B Baseline Loading% | 25.3
Total Scenarios Evaluated | 23
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 33
Switch Child Node | 6
Tie Node (TR_A side) | 6
Tie Node (TR_B side) | 29
Tie Line Distance (m) | 130.2
Load Transferred (kW) | 23.27
TR_A Loading After (%) | 57.7
TR_B Loading After (%) | 28.8
Minimum Voltage (V) | 216.4