## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 25 | 29 | 25 | 3.4 | 51.8 | 95 | 86.6 | 45.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 25 | 26 | 29 | 25 | 3.4 | 49.02 | 95 | 86.6 | 45.6 | 28 | 82.9 | 221.4 | 204.6 | 204.6 | NO
| NG | 26 | 36 | 29 | 25 | 3.4 | 46.91 | 95 | 86.6 | 45.6 | 28 | 81.2 | 221.4 | 205.2 | 205.2 | NO
| NG | 36 | 37 | 29 | 25 | 3.4 | 46.91 | 95 | 86.6 | 45.6 | 30.4 | 81.2 | 221.2 | 205.2 | 205.2 | NO
| NG | 37 | 44 | 29 | 25 | 3.4 | 38.94 | 95 | 86.6 | 45.6 | 39.6 | 75.1 | 220.6 | 206.3 | 206.3 | NO
| NG | 37 | 38 | 39 | 48 | 131.1 | 7.97 | 50 | 86.6 | 45.6 | 77.2 | 47.8 | 202.7 | 213.3 | 202.7 | NO
| NG | 44 | 78 | 29 | 25 | 3.4 | 35.76 | 95 | 86.6 | 45.6 | 43.3 | 71.7 | 220.4 | 206 | 206 | NO
| NG | 38 | 39 | 39 | 48 | 131.1 | 7.35 | 50 | 86.6 | 45.6 | 77.9 | 47.8 | 202.7 | 213.3 | 202.7 | NO
| NG | 78 | 0 | 29 | 25 | 3.4 | 34.34 | 95 | 86.6 | 45.6 | 44.9 | 71.7 | 220.1 | 206 | 206 | NO
| NG | 0 | 1 | 29 | 25 | 3.4 | 34.34 | 95 | 86.6 | 45.6 | 44.9 | 71.7 | 220.1 | 206 | 206 | NO
| NG | 1 | 72 | 29 | 25 | 3.4 | 33.66 | 95 | 86.6 | 45.6 | 45.7 | 71.2 | 220.1 | 205.9 | 205.9 | NO
| NG | 72 | 30 | 29 | 25 | 3.4 | 29.25 | 95 | 86.6 | 45.6 | 49.6 | 67.9 | 219.8 | 206.3 | 206.3 | NO
| NG | 30 | 27 | 29 | 25 | 3.4 | 29.25 | 95 | 86.6 | 45.6 | 49.6 | 67.9 | 219.8 | 206.3 | 206.3 | NO
| NG | 27 | 28 | 29 | 25 | 3.4 | 29.25 | 95 | 86.6 | 45.6 | 50.8 | 67.9 | 219.6 | 206.3 | 206.3 | NO
| NG | 28 | 33 | 29 | 25 | 3.4 | 23.35 | 95 | 86.6 | 45.6 | 57.6 | 63.5 | 219.2 | 207.3 | 207.3 | NO
| NG | 33 | 6 | 29 | 25 | 3.4 | 23.27 | 95 | 86.6 | 45.6 | 57.7 | 63.4 | 219.2 | 207.3 | 207.3 | NO
| NG | 6 | 7 | 29 | 25 | 3.4 | 23.27 | 95 | 86.6 | 45.6 | 57.7 | 3.1 | 219.2 | 6.4 | 6.4 | NO
| NG | 7 | 8 | 8 | 25 | 22.9 | 22.92 | 50 | 86.6 | 45.6 | 58.1 | 3.1 | 219.2 | 6.4 | 6.4 | NO
| NG | 8 | 79 | 79 | 25 | 25.5 | 22.92 | 50 | 86.6 | 45.6 | 58.1 | 63.1 | 219.2 | 207.8 | 207.8 | NO
1 | OK | 79 | 10 | 21 | 21 | 32.3 | 22.92 | 50 | 86.6 | 45.6 | 58.1 | 56.2 | 219.2 | 211.8 | 211.8 | YES
2 | OK | 10 | 9 | 21 | 21 | 32.3 | 22.92 | 50 | 86.6 | 45.6 | 58.1 | 56.2 | 219.2 | 211.8 | 211.8 | YES
3 | OK | 9 | 16 | 21 | 21 | 32.3 | 22.53 | 50 | 86.6 | 45.6 | 58.6 | 56.2 | 219.2 | 211.8 | 211.8 | YES
4 | OK | 16 | 15 | 21 | 21 | 32.3 | 16.72 | 50 | 86.6 | 45.6 | 65.4 | 54.7 | 218.6 | 214.8 | 214.8 | YES
5 | OK | 15 | 31 | 21 | 21 | 32.3 | 14.83 | 50 | 86.6 | 45.6 | 67.7 | 54.7 | 216.1 | 214.8 | 214.8 | YES
6 | OK | 31 | 17 | 21 | 21 | 32.3 | 14.42 | 50 | 86.6 | 45.6 | 68.2 | 54.7 | 215.4 | 214.8 | 214.8 | YES
7 | OK | 17 | 3 | 21 | 21 | 32.3 | 11.96 | 50 | 86.6 | 45.6 | 71.2 | 54.7 | 215.5 | 214.8 | 214.8 | YES
8 | ** OPTIMAL ** | 3 | 2 | 21 | 21 | 32.3 | 10.42 | 50 | 86.6 | 45.6 | 73 | 53.4 | 216.1 | 216.5 | 216.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-004667
TR_B (available) | 65-034284
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 86.6
TR_B Baseline Loading% | 45.6
Total Scenarios Evaluated | 27
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 2
Tie Node (TR_A side) | 21
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 32.3
Load Transferred (kW) | 10.42
TR_A Loading After (%) | 73
TR_B Loading After (%) | 53.4
Minimum Voltage (V) | 216.1