## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 23 | 22 | 8 | 4 | 101.5 | 21.39 | 50 | 83.9 | 5.2 | [5 empty] | NO | TR_A sim: ไม่พบสาย backbone: TAG มี 'LC'
| NG | 22 | 7 | 8 | 4 | 101.5 | 20.88 | 50 | 83.9 | 5.2 | 1.9 | 70.3 | 230.5 | 188.5 | 188.5 | NO
1 | ** OPTIMAL ** | 7 | 5 | 5 | 4 | 150.1 | 11.1 | 50 | 83.9 | 5.2 | 40 | 26.6 | 218.3 | 212.3 | 212.3 | YES
| NG | 7 | 8 | 8 | 4 | 101.5 | 9.78 | 50 | 83.9 | 5.2 | 45.6 | 45.3 | 217.6 | 206.2 | 206.2 | NO
| NG | 8 | 0 | 0 | 4 | 101.7 | 9.78 | 50 | 83.9 | 5.2 | 45.6 | 45.3 | 217.6 | 206.3 | 206.3 | NO
| NG | 0 | 1 | 1 | 4 | 112.3 | 9.33 | 50 | 83.9 | 5.2 | 47.3 | 43.1 | 217.2 | 208.4 | 208.4 | NO
2 | OK | 1 | 2 | 2 | 4 | 127.5 | 8.41 | 50 | 83.9 | 5.2 | 50.8 | 39.1 | 216.5 | 211 | 211 | YES
3 | OK | 2 | 3 | 3 | 4 | 150.3 | 8.09 | 50 | 83.9 | 5.2 | 52 | 37.7 | 216.2 | 212.1 | 212.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-005738
TR_B (available) | 66-005401
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 83.9
TR_B Baseline Loading% | 5.2
Total Scenarios Evaluated | 8
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 7
Switch Child Node | 5
Tie Node (TR_A side) | 5
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 150.1
Load Transferred (kW) | 11.1
TR_A Loading After (%) | 40
TR_B Loading After (%) | 26.6
Minimum Voltage (V) | 212.3