## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 50 | 16 | 15 | 0 | 29.1 | 7.64 | 50 | 82.5 | 45.9 | 52.9 | 75.8 | 215.9 | 217.1 | 215.9 | YES
2 | OK | 50 | 57 | 57 | 18 | 113 | 2.65 | 50 | 82.5 | 45.9 | 72.2 | 56.3 | 215.2 | 216.5 | 215.2 | YES
3 | OK | 25 | 28 | 8 | 13 | 32.4 | 9.93 | 50 | 82.5 | 45.9 | 43.6 | 68.9 | 220.7 | 215 | 215 | YES
4 | OK | 16 | 15 | 15 | 0 | 29.1 | 7.11 | 50 | 82.5 | 45.9 | 54.9 | 73.7 | 215.9 | 217.3 | 215.9 | YES
5 | OK | 28 | 27 | 8 | 13 | 32.4 | 6.85 | 50 | 82.5 | 45.9 | 55.5 | 68.9 | 220.7 | 215 | 215 | YES
6 | OK | 28 | 46 | 46 | 18 | 108.7 | 3.08 | 50 | 82.5 | 45.9 | 70.6 | 58 | 213 | 217.3 | 213 | YES
7 | OK | 15 | 23 | 0 | 37 | 60.6 | 6.69 | 50 | 82.5 | 45.9 | 56.5 | 71.9 | 215.6 | 217.7 | 215.6 | YES
8 | OK | 27 | 9 | 8 | 13 | 32.4 | 6.72 | 50 | 82.5 | 45.9 | 56 | 68.4 | 220.6 | 215.3 | 215.3 | YES
9 | OK | 46 | 45 | 45 | 18 | 140.3 | 2.55 | 50 | 82.5 | 45.9 | 72.6 | 55.9 | 213 | 218.5 | 213 | YES
10 | OK | 23 | 22 | 0 | 37 | 60.6 | 5.78 | 50 | 82.5 | 45.9 | 60 | 68.3 | 215.4 | 219.5 | 215.4 | YES
11 | OK | 9 | 8 | 8 | 13 | 32.4 | 6.72 | 50 | 82.5 | 45.9 | 56 | 68.4 | 220.6 | 215.3 | 215.3 | YES
12 | OK | 22 | 20 | 0 | 37 | 60.6 | 5.45 | 50 | 82.5 | 45.9 | 61.3 | 67 | 215.2 | 219.3 | 215.2 | YES
13 | OK | 8 | 10 | 10 | 13 | 54.8 | 5.8 | 50 | 82.5 | 45.9 | 59.5 | 65.9 | 220.1 | 216.6 | 216.6 | YES
14 | OK | 20 | 19 | 0 | 37 | 60.6 | 5.16 | 50 | 82.5 | 45.9 | 62.4 | 65.9 | 215 | 219.2 | 215 | YES
15 | OK | 10 | 26 | 6 | 31 | 58.1 | 5.33 | 50 | 82.5 | 45.9 | 61.3 | 64.4 | 219.8 | 213.8 | 213.8 | YES
16 | OK | 19 | 49 | 0 | 37 | 60.6 | 4.07 | 50 | 82.5 | 45.9 | 66.6 | 61.6 | 215 | 222.7 | 215 | YES
17 | ** OPTIMAL ** | 26 | 35 | 35 | 13 | 61.2 | 3.09 | 50 | 82.5 | 45.9 | 70.1 | 57.9 | 218.6 | 220.1 | 218.6 | YES
18 | OK | 26 | 39 | 6 | 31 | 58.1 | 2.24 | 50 | 82.5 | 45.9 | 73.5 | 51.9 | 216.5 | 222.3 | 216.5 | YES
19 | OK | 49 | 21 | 0 | 37 | 60.6 | 4.07 | 50 | 82.5 | 45.9 | 66.6 | 61.6 | 215 | 222.7 | 215 | YES
20 | OK | 35 | 36 | 36 | 13 | 82.2 | 3.01 | 50 | 82.5 | 45.9 | 70.4 | 57.6 | 218.5 | 220.4 | 218.5 | YES
21 | OK | 39 | 11 | 6 | 31 | 58.1 | 2.09 | 50 | 82.5 | 45.9 | 74.1 | 51.3 | 216.2 | 222.7 | 216.2 | YES
22 | OK | 21 | 3 | 0 | 37 | 60.6 | 3.93 | 50 | 82.5 | 45.9 | 67.1 | 61 | 215 | 222.7 | 215 | YES
23 | OK | 36 | 41 | 41 | 13 | 103 | 2.73 | 50 | 82.5 | 45.9 | 71.5 | 56.5 | 218.3 | 221 | 218.3 | YES
24 | OK | 11 | 12 | 6 | 31 | 58.1 | 1.56 | 50 | 82.5 | 45.9 | 76.2 | 51.3 | 216.2 | 222.7 | 216.2 | YES
25 | OK | 3 | 4 | 0 | 37 | 60.6 | 3.72 | 50 | 82.5 | 45.9 | 67.9 | 60.2 | 214.8 | 223.1 | 214.8 | YES
26 | OK | 41 | 14 | 14 | 13 | 139.5 | 1.87 | 50 | 82.5 | 45.9 | 74.9 | 53.1 | 217.5 | 222.6 | 217.5 | YES
27 | OK | 12 | 13 | 6 | 31 | 58.1 | 1.27 | 50 | 82.5 | 45.9 | 77.3 | 50.8 | 216 | 222.9 | 216 | YES
28 | OK | 4 | 5 | 0 | 37 | 60.6 | 3.26 | 50 | 82.5 | 45.9 | 69.7 | 58.4 | 214.8 | 223.1 | 214.8 | YES
29 | OK | 13 | 7 | 6 | 31 | 58.1 | 1.27 | 50 | 82.5 | 45.9 | 77.3 | 50.8 | 216 | 222.9 | 216 | YES
30 | OK | 5 | 0 | 0 | 37 | 60.6 | 1.99 | 50 | 82.5 | 45.9 | 74.7 | 53.5 | 213.8 | 223.7 | 213.8 | YES
31 | OK | 0 | 1 | 1 | 37 | 73.2 | 1.53 | 50 | 82.5 | 45.9 | 76.4 | 51.7 | 213.8 | 224.1 | 213.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-006167
TR_B (available) | 47-000669
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 45.9
Total Scenarios Evaluated | 31
Feasible Scenarios | 31
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 35
Tie Node (TR_A side) | 35
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 61.2
Load Transferred (kW) | 3.09
TR_A Loading After (%) | 70.1
TR_B Loading After (%) | 57.9
Minimum Voltage (V) | 218.6