## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 51 | 50 | 53 | 2 | 3.1 | 10.29 | 50 | 82.5 | 23.7 | 42.6 | 48.4 | 217.9 | 207.5 | 207.5 | NO
1 | OK | 50 | 16 | 53 | 2 | 3.1 | 7.64 | 50 | 82.5 | 23.7 | 52.9 | 37.5 | 215.9 | 218.1 | 215.9 | YES
2 | ** OPTIMAL ** | 16 | 15 | 53 | 2 | 3.1 | 7.11 | 50 | 82.5 | 23.7 | 54.9 | 37.5 | 215.9 | 218.1 | 215.9 | YES
3 | OK | 15 | 23 | 53 | 2 | 3.1 | 6.69 | 50 | 82.5 | 23.7 | 56.5 | 35.8 | 215.6 | 218.5 | 215.6 | YES
4 | OK | 23 | 22 | 53 | 2 | 3.1 | 5.78 | 50 | 82.5 | 23.7 | 60 | 35.1 | 215.4 | 218.7 | 215.4 | YES
5 | OK | 22 | 20 | 53 | 2 | 3.1 | 5.45 | 50 | 82.5 | 23.7 | 61.3 | 33.8 | 215.2 | 219 | 215.2 | YES
6 | OK | 20 | 19 | 53 | 2 | 3.1 | 5.16 | 50 | 82.5 | 23.7 | 62.4 | 32.7 | 215 | 219.3 | 215 | YES
7 | OK | 19 | 49 | 53 | 2 | 3.1 | 4.07 | 50 | 82.5 | 23.7 | 66.6 | 32.7 | 215 | 219.3 | 215 | YES
8 | OK | 49 | 21 | 53 | 2 | 3.1 | 4.07 | 50 | 82.5 | 23.7 | 66.6 | 32.7 | 215 | 219.3 | 215 | YES
9 | OK | 21 | 3 | 53 | 2 | 3.1 | 3.93 | 50 | 82.5 | 23.7 | 67.1 | 32.7 | 215 | 219.3 | 215 | YES
10 | OK | 3 | 4 | 53 | 2 | 3.1 | 3.72 | 50 | 82.5 | 23.7 | 67.9 | 31.8 | 214.8 | 219.5 | 214.8 | YES
11 | OK | 4 | 5 | 53 | 2 | 3.1 | 3.26 | 50 | 82.5 | 23.7 | 69.7 | 31.8 | 214.8 | 219.5 | 214.8 | YES
12 | OK | 5 | 0 | 53 | 2 | 3.1 | 1.99 | 50 | 82.5 | 23.7 | 74.7 | 27 | 213.8 | 220.6 | 213.8 | YES
13 | OK | 0 | 1 | 53 | 2 | 3.1 | 1.53 | 50 | 82.5 | 23.7 | 76.4 | 27 | 213.8 | 220.6 | 213.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-006167
TR_B (available) | 58-004376
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 23.7
Total Scenarios Evaluated | 14
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 15
Tie Node (TR_A side) | 53
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 3.1
Load Transferred (kW) | 7.11
TR_A Loading After (%) | 54.9
TR_B Loading After (%) | 37.5
Minimum Voltage (V) | 215.9