## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 51 | 24 | 42 | 1 | 164.4 | 10.92 | 50 | 82.5 | 3.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 24 | 25 | 42 | 1 | 164.4 | 10.38 | 50 | 82.5 | 3.8 | 41.9 | 29 | 221 | 213.4 | 213.4 | YES
2 | OK | 25 | 28 | 42 | 1 | 164.4 | 9.93 | 50 | 82.5 | 3.8 | 43.6 | 27.1 | 220.7 | 214.6 | 214.6 | YES
3 | OK | 28 | 27 | 42 | 1 | 164.4 | 6.85 | 50 | 82.5 | 3.8 | 55.5 | 27.1 | 220.7 | 214.6 | 214.6 | YES
4 | OK | 28 | 46 | 38 | 1 | 227.5 | 3.08 | 50 | 82.5 | 3.8 | 70.6 | 15.8 | 213 | 222.4 | 213 | YES
5 | ** OPTIMAL ** | 27 | 9 | 42 | 1 | 164.4 | 6.72 | 50 | 82.5 | 3.8 | 56 | 26.6 | 220.6 | 215 | 215 | YES
6 | OK | 46 | 45 | 38 | 1 | 227.5 | 2.55 | 50 | 82.5 | 3.8 | 72.6 | 13.7 | 213 | 223.4 | 213 | YES
7 | OK | 9 | 8 | 42 | 1 | 164.4 | 6.72 | 50 | 82.5 | 3.8 | 56 | 26.6 | 220.6 | 215 | 215 | YES
8 | OK | 45 | 38 | 38 | 1 | 227.5 | 2.24 | 50 | 82.5 | 3.8 | 73.8 | 12.5 | 213 | 224 | 213 | YES
9 | OK | 38 | 37 | 37 | 1 | 229.2 | 2.24 | 50 | 82.5 | 3.8 | 73.8 | 12.5 | 213 | 224.6 | 213 | YES
10 | OK | 37 | 34 | 34 | 0 | 244.6 | 2.08 | 50 | 82.5 | 3.8 | 74.4 | 11.8 | 213 | 226.1 | 213 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-006167
TR_B (available) | 63-010620
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 82.5
TR_B Baseline Loading% | 3.8
Total Scenarios Evaluated | 11
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 27
Switch Child Node | 9
Tie Node (TR_A side) | 42
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 164.4
Load Transferred (kW) | 6.72
TR_A Loading After (%) | 56
TR_B Loading After (%) | 26.6
Minimum Voltage (V) | 215