## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 1 | 14 | 22 | 4 | 37.2 | 12.45 | 50 | 86 | 19.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 14 | 4 | 22 | 4 | 37.2 | 11.15 | 50 | 86 | 19.7 | 42.2 | 26.8 | 219.8 | 212.5 | 212.5 | YES
2 | OK | 4 | 5 | 22 | 4 | 37.2 | 9.25 | 50 | 86 | 19.7 | 49.5 | 24.9 | 219.4 | 218.6 | 218.6 | YES
3 | OK | 5 | 25 | 22 | 4 | 37.2 | 8.99 | 50 | 86 | 19.7 | 50.5 | 24.6 | 219.4 | 219.6 | 219.4 | YES
4 | OK | 25 | 26 | 22 | 4 | 37.2 | 8.99 | 50 | 86 | 19.7 | 50.5 | 24.6 | 219.4 | 219.6 | 219.4 | YES
5 | ** OPTIMAL ** | 26 | 6 | 22 | 4 | 37.2 | 8.61 | 50 | 86 | 19.7 | 50.5 | 24.6 | 219.4 | 219.6 | 219.4 | YES
6 | OK | 6 | 7 | 22 | 4 | 37.2 | 8.61 | 50 | 86 | 19.7 | 51.9 | 24.6 | 219.2 | 219.6 | 219.2 | YES
7 | OK | 7 | 23 | 22 | 4 | 37.2 | 8.61 | 50 | 86 | 19.7 | 51.9 | 24.6 | 219.2 | 219.6 | 219.2 | YES
8 | OK | 23 | 24 | 22 | 4 | 37.2 | 6.58 | 50 | 86 | 19.7 | 59.7 | 23.6 | 218.2 | 220 | 218.2 | YES
9 | OK | 24 | 18 | 22 | 4 | 37.2 | 6.44 | 50 | 86 | 19.7 | 60.3 | 23.6 | 218.1 | 220 | 218.1 | YES
10 | OK | 18 | 19 | 22 | 4 | 37.2 | 6 | 50 | 86 | 19.7 | 62 | 23.6 | 217.8 | 220 | 217.8 | YES
11 | OK | 19 | 20 | 22 | 4 | 37.2 | 6 | 50 | 86 | 19.7 | 62 | 23.6 | 217.8 | 220 | 217.8 | YES
12 | OK | 20 | 8 | 22 | 4 | 37.2 | 6 | 50 | 86 | 19.7 | 62 | 23.6 | 217.8 | 220 | 217.8 | YES
13 | OK | 8 | 9 | 22 | 4 | 37.2 | 2.66 | 50 | 86 | 19.7 | 75.2 | 22.3 | 214.7 | 220.3 | 214.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-006569
TR_B (available) | 43-004657
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 86
TR_B Baseline Loading% | 19.7
Total Scenarios Evaluated | 14
Feasible Scenarios | 13
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 6
Tie Node (TR_A side) | 22
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 37.2
Load Transferred (kW) | 8.61
TR_A Loading After (%) | 50.5
TR_B Loading After (%) | 24.6
Minimum Voltage (V) | 219.4