## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 13 | 13 | 57 | 76.2 | 1.77 | 50 | 80.7 | 23.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 18 | 19 | 44 | 58 | 2.2 | 18.93 | 50 | 80.7 | 23.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 13 | 6 | 5 | 55 | 81.1 | 1.13 | 50 | 80.7 | 23.6 | 76.3 | 24.4 | 212.8 | 216.6 | 212.8 | YES
| NG | 19 | 7 | 44 | 58 | 2.2 | 18.93 | 50 | 80.7 | 23.6 | 6.7 | 32 | 230.2 | 190.4 | 190.4 | NO
2 | OK | 6 | 5 | 5 | 55 | 81.1 | 0.59 | 50 | 80.7 | 23.6 | 78.4 | 23.6 | 212.4 | 216.9 | 212.4 | YES
3 | OK | 7 | 3 | 3 | 57 | 70.2 | 1.24 | 50 | 80.7 | 23.6 | 75.9 | 24 | 212.8 | 216.6 | 212.8 | YES
| NG | 7 | 14 | 44 | 58 | 2.2 | 17.44 | 50 | 80.7 | 23.6 | 11.5 | 31.4 | 229.7 | 192.4 | 192.4 | NO
4 | OK | 3 | 4 | 4 | 57 | 71.9 | 1.24 | 50 | 80.7 | 23.6 | 75.9 | 23.6 | 212.8 | 216.9 | 212.8 | YES
| NG | 14 | 15 | 44 | 58 | 2.2 | 16.86 | 50 | 80.7 | 23.6 | 14.6 | 31.4 | 229.1 | 192.4 | 192.4 | NO
| NG | 15 | 21 | 44 | 58 | 2.2 | 16.86 | 50 | 80.7 | 23.6 | 14.6 | 31.4 | 229.1 | 192.4 | 192.4 | NO
| NG | 21 | 20 | 40 | 62 | 2.8 | 12.55 | 50 | 80.7 | 23.6 | 30.3 | 29.7 | 226.2 | 194 | 194 | NO
5 | OK | 21 | 22 | 44 | 58 | 2.2 | 4.08 | 50 | 80.7 | 23.6 | 64.7 | 25.1 | 214.7 | 215.8 | 214.7 | YES
| NG | 20 | 32 | 40 | 62 | 2.8 | 12.55 | 50 | 80.7 | 23.6 | 31.2 | 29.7 | 226 | 194 | 194 | NO
6 | OK | 22 | 23 | 23 | 59 | 3 | 0.25 | 50 | 80.7 | 23.6 | 79.7 | 23.7 | 212.5 | 216.9 | 212.5 | YES
7 | OK | 22 | 31 | 44 | 58 | 2.2 | 3.83 | 50 | 80.7 | 23.6 | 65.6 | 25 | 214.5 | 215.9 | 214.5 | YES
| NG | 32 | 43 | 40 | 62 | 2.8 | 12.55 | 50 | 80.7 | 23.6 | 31.2 | 29.7 | 226 | 194 | 194 | NO
8 | OK | 31 | 33 | 44 | 58 | 2.2 | 3.73 | 50 | 80.7 | 23.6 | 66 | 25 | 214.5 | 215.9 | 214.5 | YES
| NG | 43 | 30 | 40 | 62 | 2.8 | 12.55 | 50 | 80.7 | 23.6 | 31.2 | 29.7 | 226 | 194 | 194 | NO
9 | OK | 33 | 37 | 44 | 58 | 2.2 | 3.68 | 50 | 80.7 | 23.6 | 66.2 | 24.9 | 214.5 | 215.9 | 214.5 | YES
| NG | 30 | 12 | 40 | 62 | 2.8 | 12.55 | 50 | 80.7 | 23.6 | 31.2 | 29.7 | 226 | 194 | 194 | NO
10 | OK | 37 | 27 | 44 | 58 | 2.2 | 2.89 | 50 | 80.7 | 23.6 | 69.3 | 24.9 | 214.5 | 215.9 | 214.5 | YES
| NG | 12 | 8 | 40 | 62 | 2.8 | 11.92 | 50 | 80.7 | 23.6 | 33.6 | 29.7 | 225.3 | 194 | 194 | NO
11 | OK | 27 | 28 | 44 | 58 | 2.2 | 2.8 | 50 | 80.7 | 23.6 | 69.7 | 24.9 | 214.5 | 215.9 | 214.5 | YES
12 | OK | 8 | 9 | 40 | 62 | 2.8 | 2.03 | 50 | 80.7 | 23.6 | 72.6 | 25.1 | 215.4 | 215.8 | 215.4 | YES
13 | OK | 8 | 16 | 16 | 57 | 70.7 | 9.89 | 50 | 80.7 | 23.6 | 41.4 | 27.7 | 224.2 | 212.3 | 212.3 | YES
14 | OK | 28 | 44 | 44 | 58 | 2.2 | 1.87 | 50 | 80.7 | 23.6 | 69.7 | 24.2 | 214.5 | 216.4 | 214.5 | YES
15 | OK | 9 | 0 | 40 | 62 | 2.8 | 1.74 | 50 | 80.7 | 23.6 | 73.7 | 24.6 | 214.9 | 216.2 | 214.9 | YES
16 | OK | 16 | 17 | 17 | 57 | 77.2 | 9.08 | 50 | 80.7 | 23.6 | 44.6 | 27.7 | 224.2 | 212.4 | 212.4 | YES
17 | OK | 0 | 1 | 40 | 62 | 2.8 | 1.2 | 50 | 80.7 | 23.6 | 75.9 | 24.5 | 214.1 | 216.3 | 214.1 | YES
18 | OK | 17 | 11 | 11 | 57 | 108.9 | 9.02 | 50 | 80.7 | 23.6 | 44.8 | 27.7 | 224.2 | 212.4 | 212.4 | YES
| NG | 11 | 10 | 10 | 58 | 109.9 | 7.87 | 50 | 80.7 | 23.6 | 49.3 | 27.7 | 223.3 | 209.4 | 209.4 | NO
19 | OK | 10 | 26 | 26 | 58 | 115 | 7.8 | 50 | 80.7 | 23.6 | 49.5 | 27.7 | 223.2 | 211.3 | 211.3 | YES
20 | ** OPTIMAL ** | 26 | 34 | 34 | 58 | 126.4 | 4.7 | 50 | 80.7 | 23.6 | 61.7 | 25.2 | 218.6 | 215.7 | 215.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-007009
TR_B (available) | 54-014152
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.7
TR_B Baseline Loading% | 23.6
Total Scenarios Evaluated | 33
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 34
Tie Node (TR_A side) | 34
Tie Node (TR_B side) | 58
Tie Line Distance (m) | 126.4
Load Transferred (kW) | 4.7
TR_A Loading After (%) | 61.7
TR_B Loading After (%) | 25.2
Minimum Voltage (V) | 215.7