## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 36 | 40 | 3 | 12 | 44.2 | 3.43 | 50 | 88.8 | 21.5 | 75.5 | 35.8 | 210.4 | 208.5 | 208.5 | NO
| NG | 40 | 41 | 3 | 12 | 44.2 | 3.34 | 50 | 88.8 | 21.5 | 75.8 | 35.4 | 210.3 | 209 | 209 | NO
1 | OK | 41 | 42 | 3 | 12 | 44.2 | 3.1 | 50 | 88.8 | 21.5 | 76.7 | 34.4 | 210.1 | 210.1 | 210.1 | YES
2 | OK | 42 | 32 | 3 | 12 | 44.2 | 3.1 | 50 | 88.8 | 21.5 | 76.7 | 34.4 | 210.1 | 210.1 | 210.1 | YES
3 | OK | 32 | 23 | 3 | 12 | 44.2 | 3.1 | 50 | 88.8 | 21.5 | 76.7 | 34.4 | 210.1 | 210.1 | 210.1 | YES
4 | ** OPTIMAL ** | 23 | 22 | 3 | 12 | 44.2 | 3.1 | 50 | 88.8 | 21.5 | 76.7 | 34.4 | 210.1 | 210.1 | 210.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-008725
TR_B (available) | 54-940559
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 88.8
TR_B Baseline Loading% | 21.5
Total Scenarios Evaluated | 6
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 22
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 44.2
Load Transferred (kW) | 3.1
TR_A Loading After (%) | 76.7
TR_B Loading After (%) | 34.4
Minimum Voltage (V) | 210.1