## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 18 | 56 | 48 | 7 | 4.7 | 6.29 | 50 | 78 | 10.4 | 63.3 | 34.9 | 220.4 | 219.4 | 219.4 | YES
2 | OK | 56 | 55 | 48 | 7 | 4.7 | 6.29 | 50 | 78 | 10.4 | 63.3 | 34.9 | 220.4 | 219.4 | 219.4 | YES
3 | OK | 55 | 36 | 48 | 7 | 4.7 | 6.29 | 50 | 78 | 10.4 | 63.3 | 34.9 | 220.4 | 219.4 | 219.4 | YES
| NG | 36 | 33 | 33 | 7 | 133 | 0.17 | 50 | 78 | 10.4 | 77.7 | 11 | 59.4 | 228.1 | 59.4 | NO
4 | OK | 36 | 43 | 48 | 7 | 4.7 | 6.12 | 50 | 78 | 10.4 | 63.7 | 34.3 | 220.4 | 219.7 | 219.7 | YES
5 | OK | 43 | 42 | 48 | 7 | 4.7 | 6.12 | 50 | 78 | 10.4 | 63.7 | 34.3 | 220.4 | 219.7 | 219.7 | YES
6 | OK | 42 | 52 | 48 | 7 | 4.7 | 6.12 | 50 | 78 | 10.4 | 63.7 | 34 | 220.4 | 219.8 | 219.8 | YES
7 | OK | 52 | 46 | 48 | 7 | 4.7 | 6.03 | 50 | 78 | 10.4 | 63.9 | 33.9 | 220.4 | 219.8 | 219.8 | YES
8 | OK | 46 | 45 | 48 | 7 | 4.7 | 2.65 | 50 | 78 | 10.4 | 71.8 | 20.6 | 220.4 | 224.7 | 220.4 | YES
9 | OK | 45 | 44 | 48 | 7 | 4.7 | 2.37 | 50 | 78 | 10.4 | 72.4 | 19.5 | 220.4 | 225 | 220.4 | YES
10 | OK | 44 | 47 | 48 | 7 | 4.7 | 1.58 | 50 | 78 | 10.4 | 74.3 | 16.5 | 220.4 | 226 | 220.4 | YES
11 | OK | 47 | 48 | 48 | 7 | 4.7 | 1.58 | 50 | 78 | 10.4 | 74.3 | 16.5 | 220.4 | 226 | 220.4 | YES
12 | OK | 48 | 49 | 49 | 7 | 13.4 | 1.58 | 50 | 78 | 10.4 | 74.3 | 16.5 | 220.4 | 226 | 220.4 | YES
13 | ** OPTIMAL ** | 49 | 50 | 50 | 7 | 55 | 1.58 | 50 | 78 | 10.4 | 74.3 | 16.5 | 220.4 | 226 | 220.4 | YES
14 | OK | 50 | 51 | 51 | 7 | 57.7 | 1.58 | 50 | 78 | 10.4 | 74.3 | 10.4 | 220.4 | 228.3 | 220.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-014992
TR_B (available) | 66-006910
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 78
TR_B Baseline Loading% | 10.4
Total Scenarios Evaluated | 15
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 49
Switch Child Node | 50
Tie Node (TR_A side) | 50
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 55
Load Transferred (kW) | 1.58
TR_A Loading After (%) | 74.3
TR_B Loading After (%) | 16.5
Minimum Voltage (V) | 220.4