## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 34 | 30 | 30 | 9 | 3.4 | 2.97 | 50 | 78.3 | 52.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 30 | 31 | 31 | 9 | 41.7 | 2.97 | 50 | 78.3 | 52.5 | 67 | 63.8 | 217 | 216.9 | 216.9 | YES
2 | OK | 31 | 32 | 32 | 9 | 66 | 1.91 | 50 | 78.3 | 52.5 | 71 | 59.8 | 216.3 | 217 | 216.3 | YES
| NG | 32 | 33 | 33 | 9 | 68 | 1.03 | 50 | 78.3 | 52.5 | 74.4 | 50.8 | 215.6 | 6 | 6 | NO
3 | OK | 13 | 1 | 1 | 22 | 101.4 | 4.3 | 50 | 78.3 | 52.5 | 61.6 | 69.1 | 219 | 217 | 217 | YES
4 | OK | 13 | 43 | 46 | 12 | 37.6 | 0.81 | 50 | 78.3 | 52.5 | 75.2 | 55.7 | 215 | 215.9 | 215 | YES
| NG | 33 | 40 | 40 | 9 | 73.9 | 1.03 | 50 | 78.3 | 52.5 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 52.5% (degenerate)
5 | OK | 1 | 0 | 0 | 22 | 143.4 | 2.97 | 50 | 78.3 | 52.5 | 66.7 | 63.9 | 217.7 | 216.9 | 216.9 | YES
6 | OK | 43 | 44 | 46 | 12 | 37.6 | 0.66 | 50 | 78.3 | 52.5 | 75.8 | 55.1 | 214.8 | 215.9 | 214.8 | YES
7 | OK | 40 | 41 | 41 | 9 | 104.2 | 1 | 50 | 78.3 | 52.5 | 74.5 | 56.3 | 215.6 | 217 | 215.6 | YES
8 | ** OPTIMAL ** | 0 | 2 | 39 | 13 | 175.2 | 2.84 | 50 | 78.3 | 52.5 | 67.2 | 63.5 | 217.7 | 217.4 | 217.4 | YES
9 | OK | 41 | 42 | 42 | 9 | 108.3 | 0.77 | 50 | 78.3 | 52.5 | 75.4 | 55.4 | 215.4 | 217 | 215.4 | YES
10 | OK | 2 | 29 | 39 | 13 | 175.2 | 1.54 | 50 | 78.3 | 52.5 | 72.3 | 57.4 | 216.4 | 217.2 | 216.4 | YES
11 | OK | 7 | 11 | 11 | 9 | 125.1 | 6.2 | 50 | 78.3 | 52.5 | 54.2 | 76.6 | 217.4 | 213.2 | 213.2 | YES
12 | OK | 7 | 35 | 35 | 9 | 107.1 | 4.44 | 50 | 78.3 | 52.5 | 60.9 | 69.6 | 220.1 | 217.1 | 217.1 | YES
13 | OK | 42 | 36 | 36 | 9 | 123.7 | 0.18 | 50 | 78.3 | 52.5 | 77.6 | 53.1 | 215 | 216.9 | 215 | YES
14 | OK | 29 | 38 | 39 | 13 | 175.2 | 1.29 | 50 | 78.3 | 52.5 | 73.2 | 57.4 | 216.1 | 217.2 | 216.1 | YES
15 | OK | 11 | 12 | 28 | 9 | 157.3 | 3.56 | 50 | 78.3 | 52.5 | 64.6 | 66.3 | 214.7 | 213.7 | 213.7 | YES
16 | OK | 35 | 8 | 8 | 9 | 137.7 | 4.2 | 50 | 78.3 | 52.5 | 61.8 | 68.7 | 219.9 | 217.1 | 217.1 | YES
17 | OK | 38 | 39 | 39 | 13 | 175.2 | 1.05 | 50 | 78.3 | 52.5 | 74.2 | 56.5 | 215.9 | 217.1 | 215.9 | YES
18 | OK | 12 | 14 | 28 | 9 | 157.3 | 1.38 | 50 | 78.3 | 52.5 | 73 | 57.8 | 214.8 | 215.7 | 214.8 | YES
19 | OK | 12 | 22 | 22 | 9 | 176.2 | 2.18 | 50 | 78.3 | 52.5 | 69.9 | 60.9 | 214.7 | 215 | 214.7 | YES
20 | OK | 8 | 9 | 9 | 22 | 175.2 | 3.78 | 50 | 78.3 | 52.5 | 63.4 | 67.1 | 219.5 | 217.1 | 217.1 | YES
21 | OK | 14 | 21 | 28 | 9 | 157.3 | 1.38 | 50 | 78.3 | 52.5 | 73 | 57.8 | 214.8 | 215.7 | 214.8 | YES
| NG | 22 | 24 | 24 | 9 | 178.9 | 2.07 | 50 | 78.3 | 52.5 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
22 | OK | 9 | 10 | 10 | 22 | 203.3 | 2.11 | 50 | 78.3 | 52.5 | 70 | 60.6 | 217.8 | 217 | 217 | YES
23 | OK | 21 | 20 | 28 | 9 | 157.3 | 0.04 | 50 | 78.3 | 52.5 | 78.2 | 52.6 | 214.8 | 216.9 | 214.8 | YES
24 | OK | 24 | 23 | 23 | 9 | 196 | 1.78 | 50 | 78.3 | 52.5 | 71.4 | 59.4 | 214.8 | 215.3 | 214.8 | YES
25 | OK | 10 | 26 | 26 | 22 | 210.8 | 1.21 | 50 | 78.3 | 52.5 | 73.5 | 57.1 | 216.9 | 217 | 216.9 | YES
26 | OK | 23 | 25 | 25 | 9 | 220.1 | 1.45 | 50 | 78.3 | 52.5 | 72.7 | 58.1 | 214.8 | 215.6 | 214.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 64-019234
TR_B (available) | 64-019235
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 78.3
TR_B Baseline Loading% | 52.5
Total Scenarios Evaluated | 30
Feasible Scenarios | 26
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 2
Tie Node (TR_A side) | 39
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 175.2
Load Transferred (kW) | 2.84
TR_A Loading After (%) | 67.2
TR_B Loading After (%) | 63.5
Minimum Voltage (V) | 217.4