## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 6 | 56 | 25 | 32 | 177.7 | 18.73 | 50 | 97.7 | 34.9 | 53.3 | 47.5 | 218.4 | 206.4 | 206.4 | NO
| NG | 56 | 3 | 25 | 32 | 177.7 | 16.95 | 50 | 97.7 | 34.9 | 53.3 | 47.3 | 218.4 | 206.7 | 206.7 | NO
| NG | 3 | 2 | 25 | 32 | 177.7 | 16.95 | 50 | 97.7 | 34.9 | 57.3 | 47.3 | 218.3 | 206.7 | 206.7 | NO
1 | OK | 2 | 30 | 25 | 32 | 177.7 | 15.87 | 50 | 97.7 | 34.9 | 59.8 | 45.9 | 217.8 | 210.4 | 210.4 | YES
2 | OK | 30 | 29 | 25 | 32 | 177.7 | 15.27 | 50 | 97.7 | 34.9 | 61.2 | 45.1 | 217.5 | 212.3 | 212.3 | YES
3 | OK | 29 | 27 | 25 | 32 | 177.7 | 14.09 | 50 | 97.7 | 34.9 | 63.9 | 45.1 | 217.5 | 212.3 | 212.3 | YES
4 | OK | 27 | 28 | 25 | 32 | 177.7 | 13.74 | 50 | 97.7 | 34.9 | 64.7 | 45.1 | 217.5 | 212.3 | 212.3 | YES
5 | OK | 28 | 0 | 25 | 32 | 177.7 | 13.74 | 50 | 97.7 | 34.9 | 64.7 | 45.1 | 217.5 | 212.3 | 212.3 | YES
6 | OK | 0 | 26 | 25 | 32 | 177.7 | 12.66 | 50 | 97.7 | 34.9 | 67.2 | 45.1 | 217.5 | 212.3 | 212.3 | YES
7 | OK | 26 | 45 | 25 | 32 | 177.7 | 12.66 | 50 | 97.7 | 34.9 | 67.2 | 45.1 | 217.5 | 212.3 | 212.3 | YES
8 | ** OPTIMAL ** | 45 | 46 | 25 | 32 | 177.7 | 12.03 | 50 | 97.7 | 34.9 | 68.7 | 44.2 | 217.2 | 213.6 | 213.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-000179
TR_B (available) | 54-011010
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 97.7
TR_B Baseline Loading% | 34.9
Total Scenarios Evaluated | 11
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 45
Switch Child Node | 46
Tie Node (TR_A side) | 25
Tie Node (TR_B side) | 32
Tie Line Distance (m) | 177.7
Load Transferred (kW) | 12.03
TR_A Loading After (%) | 68.7
TR_B Loading After (%) | 44.2
Minimum Voltage (V) | 213.6