## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 6 | 7 | 22 | 0 | 3 | 18.87 | 50 | 97.7 | 7.1 | 53.5 | 51.5 | 210.7 | 214.7 | 210.7 | YES
| NG | 6 | 56 | 57 | 3 | 55.7 | 18.73 | 50 | 97.7 | 7.1 | 53.3 | 32.2 | 218.4 | 204.7 | 204.7 | NO
2 | OK | 7 | 22 | 22 | 0 | 3 | 18.87 | 50 | 97.7 | 7.1 | 53.5 | 51.5 | 210.7 | 214.7 | 210.7 | YES
| NG | 56 | 3 | 3 | 0 | 63.9 | 16.95 | 50 | 97.7 | 7.1 | 53.3 | 48.2 | 218.4 | 202.6 | 202.6 | NO
3 | OK | 22 | 8 | 8 | 0 | 10.1 | 18.87 | 50 | 97.7 | 7.1 | 53.5 | 51.5 | 210.7 | 214.8 | 210.7 | YES
| NG | 3 | 2 | 30 | 0 | 81.5 | 16.95 | 50 | 97.7 | 7.1 | 57.3 | 48.1 | 218.3 | 203 | 203 | NO
4 | OK | 8 | 9 | 9 | 0 | 36.2 | 18.87 | 50 | 97.7 | 7.1 | 53.5 | 51.5 | 210.7 | 214.8 | 210.7 | YES
| NG | 2 | 30 | 30 | 0 | 81.5 | 15.87 | 50 | 97.7 | 7.1 | 59.8 | 45.4 | 217.8 | 204.6 | 204.6 | NO
| NG | 9 | 10 | 10 | 0 | 40 | 16.62 | 50 | 97.7 | 7.1 | 58.7 | 42 | 209.5 | 219.2 | 209.5 | NO
| NG | 30 | 29 | 29 | 0 | 85.3 | 15.27 | 50 | 97.7 | 7.1 | 61.2 | 43.9 | 217.5 | 206.3 | 206.3 | NO
| NG | 10 | 12 | 12 | 0 | 69.3 | 14.06 | 50 | 97.7 | 7.1 | 64.6 | 40.1 | 208.6 | 219.1 | 208.6 | NO
| NG | 29 | 27 | 27 | 0 | 160.5 | 14.09 | 50 | 97.7 | 7.1 | 63.9 | 41 | 217.5 | 207.9 | 207.9 | NO
| NG | 12 | 17 | 17 | 0 | 74.5 | 10.15 | 50 | 97.7 | 7.1 | 73.6 | 29.4 | 208.6 | 218.9 | 208.6 | NO
5 | OK | 27 | 28 | 45 | 0 | 176.8 | 13.74 | 50 | 97.7 | 7.1 | 64.7 | 39.7 | 217.5 | 213 | 213 | YES
| NG | 17 | 37 | 37 | 0 | 84.5 | 9.53 | 50 | 97.7 | 7.1 | 75.1 | 29.4 | 208.6 | 218.9 | 208.6 | NO
6 | OK | 28 | 0 | 45 | 0 | 176.8 | 13.74 | 50 | 97.7 | 7.1 | 64.7 | 39.7 | 217.5 | 213 | 213 | YES
7 | OK | 0 | 26 | 45 | 0 | 176.8 | 12.66 | 50 | 97.7 | 7.1 | 67.2 | 37.2 | 217.5 | 212.9 | 212.9 | YES
8 | OK | 26 | 45 | 45 | 0 | 176.8 | 12.66 | 50 | 97.7 | 7.1 | 67.2 | 37.2 | 217.5 | 212.9 | 212.9 | YES
9 | ** OPTIMAL ** | 45 | 46 | 46 | 0 | 178.4 | 12.03 | 50 | 97.7 | 7.1 | 68.7 | 35.6 | 217.2 | 214.4 | 214.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-000179
TR_B (available) | 64-016582
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 97.7
TR_B Baseline Loading% | 7.1
Total Scenarios Evaluated | 19
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 45
Switch Child Node | 46
Tie Node (TR_A side) | 46
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 178.4
Load Transferred (kW) | 12.03
TR_A Loading After (%) | 68.7
TR_B Loading After (%) | 35.6
Minimum Voltage (V) | 214.4