## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 14 | 13 | 77 | 55.9 | 10.2 | 50 | 90.2 | 28.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 14 | 15 | 13 | 77 | 55.9 | 8.76 | 50 | 90.2 | 28.7 | 55.6 | 32.8 | 213.9 | 215.2 | 213.9 | YES
2 | OK | 15 | 9 | 13 | 77 | 55.9 | 8.76 | 50 | 90.2 | 28.7 | 55.6 | 32.8 | 213.9 | 215.2 | 213.9 | YES
3 | ** OPTIMAL ** | 9 | 10 | 13 | 77 | 55.9 | 8.5 | 50 | 90.2 | 28.7 | 55.6 | 32.8 | 213.9 | 215.2 | 213.9 | YES
4 | OK | 10 | 19 | 13 | 77 | 55.9 | 7.09 | 50 | 90.2 | 28.7 | 62 | 32.1 | 213.7 | 215.2 | 213.7 | YES
5 | OK | 19 | 20 | 13 | 77 | 55.9 | 6.34 | 50 | 90.2 | 28.7 | 64.9 | 31.7 | 213.7 | 215.2 | 213.7 | YES
6 | OK | 20 | 21 | 13 | 77 | 55.9 | 6.04 | 50 | 90.2 | 28.7 | 66 | 31.6 | 213.7 | 215.2 | 213.7 | YES
7 | OK | 21 | 25 | 13 | 77 | 55.9 | 4.67 | 50 | 90.2 | 28.7 | 71.4 | 30.9 | 213.7 | 215.2 | 213.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-003300
TR_B (available) | 63-007762
TR_A Rated kVA | 30
TR_B Rated kVA | 250
TR_A Baseline Loading% | 90.2
TR_B Baseline Loading% | 28.7
Total Scenarios Evaluated | 8
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 9
Switch Child Node | 10
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 77
Tie Line Distance (m) | 55.9
Load Transferred (kW) | 8.5
TR_A Loading After (%) | 55.6
TR_B Loading After (%) | 32.8
Minimum Voltage (V) | 213.9