## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 16 | 14 | 15 | 0 | 5.2 | 10.2 | 50 | 90.2 | 10.4 | 50.1 | 16.1 | 214.8 | 227 | 214.8 | YES
| NG | 16 | 17 | 17 | 0 | 110.4 | 12.8 | 50 | 90.2 | 10.4 | 40.1 | 36 | 215.2 | 209.6 | 209.6 | NO
2 | OK | 14 | 15 | 15 | 0 | 5.2 | 8.76 | 50 | 90.2 | 10.4 | 55.6 | 11.4 | 213.9 | 228.1 | 213.9 | YES
3 | OK | 17 | 18 | 18 | 0 | 220 | 10.26 | 50 | 90.2 | 10.4 | 49.8 | 35.8 | 213.2 | 211 | 211 | YES
4 | OK | 15 | 9 | 9 | 0 | 14.3 | 8.76 | 50 | 90.2 | 10.4 | 55.6 | 11.4 | 213.9 | 228.1 | 213.9 | YES
5 | OK | 9 | 10 | 10 | 0 | 16.3 | 8.5 | 50 | 90.2 | 10.4 | 55.6 | 10.4 | 213.9 | 228.3 | 213.9 | YES
6 | OK | 10 | 19 | 19 | 0 | 69.5 | 7.09 | 50 | 90.2 | 10.4 | 62 | 38.4 | 213.7 | 215.3 | 213.7 | YES
7 | OK | 19 | 20 | 20 | 0 | 121 | 6.34 | 50 | 90.2 | 10.4 | 64.9 | 35.4 | 213.7 | 216.5 | 213.7 | YES
8 | OK | 20 | 21 | 21 | 0 | 159.6 | 6.04 | 50 | 90.2 | 10.4 | 66 | 34.2 | 213.7 | 217 | 213.7 | YES
9 | OK | 21 | 25 | 25 | 0 | 195.8 | 4.67 | 50 | 90.2 | 10.4 | 71.4 | 28.6 | 213.7 | 219.5 | 213.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-003300
TR_B (available) | 66-006910
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 90.2
TR_B Baseline Loading% | 10.4
Total Scenarios Evaluated | 10
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 14
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 0
Tie Line Distance (m) | 5.2
Load Transferred (kW) | 10.2
TR_A Loading After (%) | 50.1
TR_B Loading After (%) | 16.1
Minimum Voltage (V) | 214.8