## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 17 | 7 | 17 | 139.2 | 12.8 | 50 | 90.2 | 44.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 17 | 18 | 7 | 17 | 139.2 | 10.26 | 50 | 90.2 | 44.1 | 49.8 | 51.8 | 213.2 | 213.5 | 213.2 | YES
2 | OK | 18 | 1 | 7 | 17 | 139.2 | 10.1 | 50 | 90.2 | 44.1 | 50.4 | 51.8 | 213.1 | 213.5 | 213.1 | YES
3 | OK | 1 | 0 | 7 | 17 | 139.2 | 8.33 | 50 | 90.2 | 44.1 | 57.2 | 49.5 | 213.1 | 218.4 | 213.1 | YES
4 | OK | 0 | 8 | 7 | 17 | 139.2 | 5.91 | 50 | 90.2 | 44.1 | 66.5 | 49.5 | 211.1 | 218.4 | 211.1 | YES
5 | OK | 8 | 3 | 7 | 17 | 139.2 | 5.91 | 50 | 90.2 | 44.1 | 66.5 | 49.5 | 211.1 | 218.4 | 211.1 | YES
| NG | 3 | 2 | 7 | 17 | 139.2 | 4.41 | 50 | 90.2 | 44.1 | 72 | 49.4 | 210 | 218.7 | 210 | NO
6 | OK | 2 | 4 | 7 | 17 | 139.2 | 3.78 | 50 | 90.2 | 44.1 | 74.9 | 48.6 | 210 | 219.7 | 210 | YES
7 | OK | 4 | 5 | 7 | 17 | 139.2 | 3.49 | 50 | 90.2 | 44.1 | 76.1 | 48.2 | 210 | 219.7 | 210 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-003300
TR_B (available) | 66-024892
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 90.2
TR_B Baseline Loading% | 44.1
Total Scenarios Evaluated | 9
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 18
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 139.2
Load Transferred (kW) | 10.26
TR_A Loading After (%) | 49.8
TR_B Loading After (%) | 51.8
Minimum Voltage (V) | 213.2