## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 69 | 68 | 18 | 58 | 2.6 | 2.51 | 50 | 58.6 | 38.6 | 49 | 48.5 | 212.9 | 213.8 | 212.9 | YES
2 | OK | 10 | 71 | 71 | 58 | 140.7 | 0.03 | 50 | 58.6 | 38.6 | 58.6 | 38.7 | 210.9 | 215.7 | 210.9 | YES
3 | OK | 68 | 18 | 18 | 58 | 2.6 | 0.88 | 50 | 58.6 | 38.6 | 49 | 42.1 | 212.9 | 215.1 | 212.9 | YES
4 | OK | 71 | 70 | 70 | 58 | 144.5 | 0.02 | 50 | 58.6 | 38.6 | 58.6 | 38.7 | 210.9 | 215.7 | 210.9 | YES
5 | ** OPTIMAL ** | 18 | 54 | 54 | 58 | 43.4 | 0.88 | 50 | 58.6 | 38.6 | 49 | 42.1 | 212.9 | 215.1 | 212.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 65-004001
TR_B (available) | 49-014395
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 58.6
TR_B Baseline Loading% | 38.6
Total Scenarios Evaluated | 5
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 18
Switch Child Node | 54
Tie Node (TR_A side) | 54
Tie Node (TR_B side) | 58
Tie Line Distance (m) | 43.4
Load Transferred (kW) | 0.88
TR_A Loading After (%) | 49
TR_B Loading After (%) | 42.1
Minimum Voltage (V) | 212.9