## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 69 | 10 | 29 | 135 | 3.8 | 19.5 | 50 | 58.6 | 25.2 | 15.5 | 30.6 | 48.9 | 212.3 | 48.9 | NO
| NG | 10 | 16 | 40 | 136 | 58.6 | 13.23 | 50 | 58.6 | 25.2 | 28.9 | 31.9 | 223.5 | 201.4 | 201.4 | NO
| NG | 10 | 67 | 29 | 135 | 3.8 | 2.81 | 50 | 58.6 | 25.2 | 56.1 | 25.2 | 207.9 | 224.3 | 207.9 | NO
| NG | 16 | 15 | 40 | 136 | 58.6 | 13.23 | 50 | 58.6 | 25.2 | 28.9 | 31.9 | 223.5 | 201.4 | 201.4 | NO
| NG | 67 | 61 | 29 | 135 | 3.8 | 2.81 | 50 | 58.6 | 25.2 | 56.1 | 25.2 | 207.9 | 224.3 | 207.9 | NO
| NG | 15 | 23 | 40 | 136 | 58.6 | 13.23 | 50 | 58.6 | 25.2 | 31.7 | 31.9 | 222.9 | 201.4 | 201.4 | NO
| NG | 61 | 60 | 29 | 135 | 3.8 | 2.09 | 50 | 58.6 | 25.2 | 59.1 | 25.2 | 206.3 | 224.3 | 206.3 | NO
| NG | 23 | 20 | 40 | 136 | 58.6 | 13.23 | 50 | 58.6 | 25.2 | 31.7 | 31.9 | 222.9 | 201.4 | 201.4 | NO
| NG | 60 | 29 | 29 | 135 | 3.8 | 0.88 | 50 | 58.6 | 25.2 | 59.1 | 25.2 | 206.3 | 224.3 | 206.3 | NO
1 | OK | 20 | 21 | 21 | 135 | 106.3 | 2.29 | 50 | 58.6 | 25.2 | 57.1 | 26.3 | 211.3 | 222.5 | 211.3 | YES
2 | OK | 20 | 22 | 22 | 135 | 113.2 | 3.35 | 50 | 58.6 | 25.2 | 52.8 | 26.8 | 213.5 | 222.5 | 213.5 | YES
| NG | 20 | 27 | 57 | 135 | 71.2 | 2.32 | 50 | 58.6 | 25.2 | 56.6 | 26.3 | 207.9 | 223.4 | 207.9 | NO
3 | ** OPTIMAL ** | 20 | 26 | 40 | 136 | 58.6 | 5.27 | 50 | 58.6 | 25.2 | 41 | 27.7 | 219.6 | 220 | 219.6 | YES
| NG | 29 | 28 | 28 | 135 | 25.2 | 0.88 | 50 | 58.6 | 25.2 | 59.1 | 25.6 | 206.3 | 224.1 | 206.3 | NO
4 | OK | 21 | 25 | 25 | 135 | 107.7 | 0.95 | 50 | 58.6 | 25.2 | 57.1 | 25.7 | 211.3 | 224.2 | 211.3 | YES
5 | OK | 22 | 53 | 53 | 135 | 115.9 | 3.35 | 50 | 58.6 | 25.2 | 52.8 | 26.3 | 213.5 | 224.1 | 213.5 | YES
| NG | 27 | 57 | 57 | 135 | 71.2 | 0.76 | 50 | 58.6 | 25.2 | 59.2 | 25.6 | 206.3 | 224.2 | 206.3 | NO
6 | OK | 26 | 38 | 37 | 136 | 92.2 | 0.33 | 50 | 58.6 | 25.2 | 57.2 | 25.4 | 211.6 | 224.3 | 211.6 | YES
7 | OK | 26 | 43 | 40 | 136 | 58.6 | 2.58 | 50 | 58.6 | 25.2 | 51.8 | 26.4 | 214.2 | 224.1 | 214.2 | YES
8 | OK | 26 | 55 | 55 | 135 | 128.1 | 2.36 | 50 | 58.6 | 25.2 | 49 | 26.3 | 215.8 | 224 | 215.8 | YES
| NG | 28 | 49 | 49 | 135 | 28.2 | 0.68 | 50 | 58.6 | 25.2 | [5 empty] | NO | TR_A sim: loading 2932786779971045287360095832574321638078622246803241963249852162518940933923526793909639016209978148743997124469370415692644352% (degenerate)
| NG | 43 | 45 | 39 | 136 | 117.2 | 0.8 | 50 | 58.6 | 25.2 | 52.9 | 25.6 | 45.9 | 224.2 | 45.9 | NO
9 | OK | 43 | 63 | 40 | 136 | 58.6 | 1.46 | 50 | 58.6 | 25.2 | 54.5 | 25.4 | 212.9 | 224.3 | 212.9 | YES
| NG | 45 | 44 | 39 | 136 | 117.2 | 0.8 | 50 | 58.6 | 25.2 | 55.9 | 25.6 | 45.6 | 224.2 | 45.6 | NO
10 | OK | 63 | 65 | 40 | 136 | 58.6 | 0.27 | 50 | 58.6 | 25.2 | 57.5 | 25.4 | 211.5 | 224.3 | 211.5 | YES
| NG | 44 | 30 | 39 | 136 | 117.2 | 0.28 | 50 | 58.6 | 25.2 | 57.4 | 25.4 | 45.4 | 224.3 | 45.4 | NO
11 | OK | 65 | 56 | 40 | 136 | 58.6 | 0.27 | 50 | 58.6 | 25.2 | 57.5 | 25.4 | 211.5 | 224.3 | 211.5 | YES
| NG | 30 | 31 | 39 | 136 | 117.2 | 0.04 | 50 | 58.6 | 25.2 | 58.4 | 25.2 | 45.3 | 224.3 | 45.3 | NO
12 | OK | 56 | 40 | 40 | 136 | 58.6 | 0.27 | 50 | 58.6 | 25.2 | 57.5 | 25.4 | 211.5 | 224.3 | 211.5 | YES
| NG | 31 | 39 | 39 | 136 | 117.2 | 0.02 | 50 | 58.6 | 25.2 | 58.5 | 25.2 | 45.3 | 224.3 | 45.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 65-004001
TR_B (available) | 53-921116
TR_A Rated kVA | 30
TR_B Rated kVA | 250
TR_A Baseline Loading% | 58.6
TR_B Baseline Loading% | 25.2
Total Scenarios Evaluated | 30
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 20
Switch Child Node | 26
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 136
Tie Line Distance (m) | 58.6
Load Transferred (kW) | 5.27
TR_A Loading After (%) | 41
TR_B Loading After (%) | 27.7
Minimum Voltage (V) | 219.6