## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 10 | 9 | 3 | 24 | 70.6 | 5.85 | 50 | 76 | 47.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 9 | 52 | 3 | 24 | 70.6 | 5.85 | 50 | 76 | 47.8 | 69.3 | 52.1 | 207.6 | 217 | 207.6 | NO
1 | OK | 43 | 51 | 55 | 24 | 20.3 | 42.39 | 50 | 76 | 47.8 | 25.5 | 48.5 | 225.5 | 217.3 | 217.3 | YES
| NG | 52 | 38 | 3 | 24 | 70.6 | 5.85 | 50 | 76 | 47.8 | 69.3 | 52.1 | 207.6 | 217 | 207.6 | NO
2 | ** OPTIMAL ** | 51 | 23 | 55 | 24 | 20.3 | 42.38 | 50 | 76 | 47.8 | 25.5 | 48.5 | 225.5 | 217.3 | 217.3 | YES
| NG | 38 | 33 | 3 | 24 | 70.6 | 5.39 | 50 | 76 | 47.8 | 69.8 | 51.8 | 207.4 | 217.1 | 207.4 | NO
| NG | 23 | 24 | 4 | 24 | 77.1 | 39.37 | 50 | 76 | 47.8 | 29 | 54.9 | 225.4 | 209.7 | 209.7 | NO
| NG | 23 | 54 | 55 | 24 | 20.3 | 3.01 | 50 | 76 | 47.8 | 72.6 | 48.3 | 207.2 | 217.3 | 207.2 | NO
| NG | 33 | 34 | 3 | 24 | 70.6 | 5.39 | 50 | 76 | 47.8 | 69.8 | 51 | 207.4 | 217.2 | 207.4 | NO
3 | OK | 24 | 25 | 4 | 24 | 77.1 | 37.97 | 50 | 76 | 47.8 | 30.6 | 53.7 | 225.4 | 213.1 | 213.1 | YES
| NG | 54 | 50 | 55 | 24 | 20.3 | 2.6 | 50 | 76 | 47.8 | 73 | 48.3 | 207.2 | 217.3 | 207.2 | NO
| NG | 34 | 1 | 3 | 24 | 70.6 | 3.89 | 50 | 76 | 47.8 | 71.6 | 50.6 | 207.3 | 217.2 | 207.3 | NO
4 | OK | 25 | 11 | 4 | 24 | 77.1 | 37.97 | 50 | 76 | 47.8 | 30.6 | 53.7 | 225.4 | 213.1 | 213.1 | YES
| NG | 50 | 41 | 55 | 24 | 20.3 | 2.6 | 50 | 76 | 47.8 | 73 | 48.3 | 207.2 | 217.3 | 207.2 | NO
| NG | 1 | 2 | 3 | 24 | 70.6 | 3.67 | 50 | 76 | 47.8 | 71.8 | 50.5 | 207.3 | 217.2 | 207.3 | NO
| NG | 11 | 8 | 8 | 24 | 138.5 | 0.23 | 50 | 76 | 47.8 | 75.8 | 48 | 207 | 217.3 | 207 | NO
| NG | 11 | 17 | 0 | 82 | 113 | 30.01 | 50 | 76 | 47.8 | 39.8 | 78.2 | 223.6 | 154.4 | 154.4 | NO
| NG | 11 | 12 | 4 | 24 | 77.1 | 7.73 | 50 | 76 | 47.8 | 67.1 | 53.7 | 207 | 213.1 | 207 | NO
| NG | 41 | 42 | 55 | 24 | 20.3 | 1.72 | 50 | 76 | 47.8 | 74 | 48.3 | 207.2 | 217.3 | 207.2 | NO
| NG | 2 | 3 | 3 | 24 | 70.6 | 2.49 | 50 | 76 | 47.8 | 73.2 | 49.6 | 207.3 | 217.2 | 207.3 | NO
| NG | 17 | 14 | 0 | 82 | 113 | 21.29 | 50 | 76 | 47.8 | 49.9 | 66.4 | 223.1 | 183.4 | 183.4 | NO
| NG | 12 | 13 | 4 | 24 | 77.1 | 6.24 | 50 | 76 | 47.8 | 68.8 | 52.5 | 207 | 216.4 | 207 | NO
| NG | 14 | 5 | 0 | 82 | 113 | 20.73 | 50 | 76 | 47.8 | 50.5 | 65.8 | 222.8 | 184.8 | 184.8 | NO
| NG | 13 | 4 | 4 | 24 | 77.1 | 4.42 | 50 | 76 | 47.8 | 70.9 | 51.1 | 207 | 217.3 | 207 | NO
| NG | 5 | 6 | 0 | 82 | 113 | 13.33 | 50 | 76 | 47.8 | 59.3 | 58.5 | 218.9 | 200.6 | 200.6 | NO
| NG | 6 | 0 | 0 | 82 | 113 | 2.39 | 50 | 76 | 47.8 | 73 | 49.6 | 208.9 | 217 | 208.9 | NO
| NG | 6 | 40 | 40 | 82 | 149.3 | 2.8 | 50 | 76 | 47.8 | 72.4 | 49.9 | 209.3 | 216.9 | 209.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 65-005463
TR_B (available) | 50-007406
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 76
TR_B Baseline Loading% | 47.8
Total Scenarios Evaluated | 27
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 51
Switch Child Node | 23
Tie Node (TR_A side) | 55
Tie Node (TR_B side) | 24
Tie Line Distance (m) | 20.3
Load Transferred (kW) | 42.38
TR_A Loading After (%) | 25.5
TR_B Loading After (%) | 48.5
Minimum Voltage (V) | 217.3