## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 15 | 13 | 78 | 63 | 83.4 | 2.05 | 50 | 78.8 | 55.2 | 77.3 | 57.8 | 206.5 | 213.5 | 206.5 | NO
| NG | 13 | 14 | 78 | 63 | 83.4 | 1.91 | 50 | 78.8 | 55.2 | 77.4 | 57.6 | 206.4 | 213.9 | 206.4 | NO
| NG | 60 | 66 | 63 | 39 | 98.6 | 6.89 | 50 | 78.8 | 55.2 | 73.6 | 63.9 | 209.1 | 211 | 209.1 | NO
| NG | 9 | 10 | 51 | 66 | 120.6 | 4.95 | 50 | 78.8 | 55.2 | 75 | 61.7 | 206.9 | 206.2 | 206.2 | NO
| NG | 66 | 61 | 61 | 39 | 141.5 | 2.35 | 50 | 78.8 | 55.2 | 77 | 58.1 | 207.1 | 215.7 | 207.1 | NO
| NG | 66 | 62 | 63 | 39 | 98.6 | 4.54 | 50 | 78.8 | 55.2 | 75.3 | 60.8 | 208.1 | 213.4 | 208.1 | NO
| NG | 67 | 28 | 68 | 2 | 2.8 | 22.17 | 50 | 78.8 | 55.2 | 62.1 | 82 | 213.2 | 213 | 213 | NO
| NG | 10 | 51 | 51 | 66 | 120.6 | 3.52 | 50 | 78.8 | 55.2 | 76.1 | 59.7 | 206.7 | 209.9 | 206.7 | NO
| NG | 62 | 63 | 63 | 39 | 98.6 | 3.59 | 50 | 78.8 | 55.2 | 76 | 59.6 | 207.7 | 214.4 | 207.7 | NO
1 | OK | 28 | 29 | 68 | 2 | 2.8 | 19.54 | 50 | 78.8 | 55.2 | 63.9 | 78.7 | 213.2 | 213.7 | 213.2 | YES
| NG | 7 | 8 | 50 | 66 | 145.1 | 4.99 | 50 | 78.8 | 55.2 | 75 | 61.4 | 206.6 | 210.1 | 206.6 | NO
2 | OK | 29 | 30 | 68 | 2 | 2.8 | 18.75 | 50 | 78.8 | 55.2 | 64.5 | 77.7 | 213.2 | 213.7 | 213.2 | YES
| NG | 65 | 18 | 18 | 37 | 161.7 | 7.26 | 50 | 78.8 | 55.2 | 73.3 | 63.9 | 205.4 | 215.4 | 205.4 | NO
| NG | 65 | 64 | 64 | 37 | 140.1 | 20.15 | 50 | 78.8 | 55.2 | 59.9 | 80.4 | 210.5 | 203.4 | 203.4 | NO
| NG | 8 | 49 | 50 | 66 | 145.1 | 3.76 | 50 | 78.8 | 55.2 | 75.9 | 59.9 | 206.6 | 210.1 | 206.6 | NO
3 | OK | 30 | 31 | 68 | 2 | 2.8 | 18.57 | 50 | 78.8 | 55.2 | 64.6 | 77.5 | 213.2 | 213.7 | 213.2 | YES
| NG | 18 | 17 | 17 | 39 | 177.1 | 6.46 | 50 | 78.8 | 55.2 | 73.9 | 63 | 205.5 | 215.2 | 205.5 | NO
| NG | 64 | 20 | 20 | 36 | 146.3 | 18.03 | 50 | 78.8 | 55.2 | 65 | 77.2 | 208.5 | 210.8 | 208.5 | NO
| NG | 49 | 50 | 50 | 66 | 145.1 | 3.05 | 50 | 78.8 | 55.2 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 55.2% (degenerate)
4 | OK | 31 | 32 | 68 | 2 | 2.8 | 18.57 | 50 | 78.8 | 55.2 | 64.6 | 77.5 | 213.2 | 213.7 | 213.2 | YES
| NG | 20 | 21 | 21 | 36 | 149.4 | 16.91 | 50 | 78.8 | 55.2 | 65.8 | 75.8 | 208 | 210.7 | 208 | NO
5 | ** OPTIMAL ** | 32 | 33 | 68 | 2 | 2.8 | 17.89 | 50 | 78.8 | 55.2 | 65.1 | 76.6 | 213.2 | 213.6 | 213.2 | YES
| NG | 21 | 22 | 22 | 36 | 156.5 | 2.1 | 50 | 78.8 | 55.2 | 77.1 | 57.7 | 207.2 | 216.8 | 207.2 | NO
| NG | 21 | 24 | 24 | 35 | 172.7 | 14.81 | 50 | 78.8 | 55.2 | 67.4 | 73.2 | 207 | 211.2 | 207 | NO
6 | OK | 33 | 34 | 68 | 2 | 2.8 | 16.91 | 50 | 78.8 | 55.2 | 65.8 | 75.5 | 213.2 | 213.6 | 213.2 | YES
| NG | 24 | 23 | 23 | 35 | 176.4 | 6.79 | 50 | 78.8 | 55.2 | 70.6 | 63.2 | 205 | 218.5 | 205 | NO
| NG | 24 | 25 | 25 | 35 | 173.2 | 4.99 | 50 | 78.8 | 55.2 | 74.9 | 60 | 208 | 215.7 | 208 | NO
7 | OK | 34 | 35 | 68 | 2 | 2.8 | 15.52 | 50 | 78.8 | 55.2 | 66.9 | 73.8 | 213.1 | 214.4 | 213.1 | YES
8 | OK | 35 | 36 | 68 | 2 | 2.8 | 13.21 | 50 | 78.8 | 55.2 | 68.6 | 70.9 | 212.8 | 216.1 | 212.8 | YES
9 | OK | 36 | 37 | 37 | 2 | 72.6 | 13.21 | 50 | 78.8 | 55.2 | 68.6 | 71 | 212.8 | 216.1 | 212.8 | YES
10 | OK | 37 | 38 | 38 | 2 | 98 | 11 | 50 | 78.8 | 55.2 | 70.2 | 68.3 | 212.7 | 216.3 | 212.7 | YES
11 | OK | 38 | 70 | 70 | 2 | 103 | 10.13 | 50 | 78.8 | 55.2 | 70.9 | 65.3 | 212.5 | 216.4 | 212.5 | YES
12 | OK | 70 | 71 | 71 | 2 | 112.6 | 5.79 | 50 | 78.8 | 55.2 | 73.4 | 61.5 | 212.6 | 216.8 | 212.6 | YES
| NG | 71 | 75 | 75 | 2 | 117.7 | 1.13 | 50 | 78.8 | 55.2 | 77.8 | 56.5 | 208.1 | 217.7 | 208.1 | NO
| NG | 75 | 74 | 74 | 2 | 126.6 | 1.13 | 50 | 78.8 | 55.2 | 77.8 | 56.5 | 208.1 | 217.7 | 208.1 | NO
| NG | 74 | 73 | 73 | 2 | 141.6 | 0.11 | 50 | 78.8 | 55.2 | 78.7 | 55.3 | 206.3 | 218 | 206.3 | NO
| NG | 73 | 76 | 76 | 2 | 145.3 | 0.11 | 50 | 78.8 | 55.2 | 78.7 | 55.2 | 206.3 | 218 | 206.3 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 65-006196
TR_B (available) | 63-027015
TR_A Rated kVA | 160
TR_B Rated kVA | 100
TR_A Baseline Loading% | 78.8
TR_B Baseline Loading% | 55.2
Total Scenarios Evaluated | 37
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 32
Switch Child Node | 33
Tie Node (TR_A side) | 68
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 2.8
Load Transferred (kW) | 17.89
TR_A Loading After (%) | 65.1
TR_B Loading After (%) | 76.6
Minimum Voltage (V) | 213.2